## ZBIRNA REKAPITULACIJA-SUMMARY
Program obrazovanja Crne Gore/ Education program of Montenegro
PREDMJER - IZGRADNJA NOVE OŠ "VLADIMIR NAZOR" / BILL OF QUANTITY - CONSTRUCTION OF NEW ELEMENTARY SCHOOL "VLADIMIR NAZOR"
Projekat | Naziv |  |  | EUR
0 | OPSTE STAVKE | GENERAL ITEMS | Ukupno/ Total | 0
1.1. | ARHITEKTONSKO GRAĐEVINSKI RADOVI | ARCHITECTURAL CONSTRUCTION WORKS | Ukupno/ Total | 0
1.2. | UREĐENJE TERENA | LANDSCAPING - ARCHITECTURE | Ukupno/ Total | 0
2.2. | VODOVOD I KANALIZACIJA | WATER SUPPLY AND SEVAGE INSTALLATION | Ukupno/ Total | 0
2.3. | PROJEKAT SAOBRAĆAJA | TRAFFIC DESIGN | Ukupno/ Total | 0
3.1.1. | JAKA STRUJA | HIGH VOLTAGE INSTALLATION | Ukupno/ Total | 0
3.1.2. | JAKA STRUJA UREĐENJE TERENA | HIGH VOLTAGE INSTALLATION OF LANDSCAPING | Ukupno/ Total | 0
3.2. | SLABA STRUJA | LOW VOLTAGE INSTALLATION | Ukupno/ Total | 0
3.3. | BMS I EMP | BMS AND EMP | Ukupno/ Total | 0
4.1. | TERMOTEHNIČKE INSTALACIJE | THERMOTECHNICAL INSTALLATION (HVAC) | Ukupno/ Total | 0
4.2. | INSTALACIJE ZA GAŠENJE POŽARA | STABLE FIRE EXTINGUISHING INSTALLATIONS | Ukupno/ Total | 0
5 . | ZAŠTITA OD POŽARA | FIRE PROTECTION | Ukupno/ Total | 0
9 . | PEJZAŽNA ARHITEKTURA | LANDSCAPING-SCENERY | Ukupno/ Total | 0
10 . | SAOBRAĆAJNA SIGNALIZACIJA | TRAFFIC SIGNALIZATION | Ukupno/ Total | 0
11 . | PROJEKAT OPREMANJA | DESIGN OF FURNITURE AND EQUIPMENT FOR SCHOOL AND HALL | Ukupno/ Total | 0
UKUPNO Predmjer i predracun/ TOTAL BoQ |  |  |  | 0
Provizorna suma (Nepredvidjeno)/Provisional Sum (Contingency) 10% |  |  |  | 0
Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING |  |  |  |  | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING | Construction of indoor complex of Administration for Execution of Criminal Sanctions - MULTIFUNCTIONAL BUILDING
KRAJNI TOTAL/GRAND TOTAL |  |  |  | 0

## 0. General Items
Program obrazovanja Crne Gore/ Education program of Montenegro
Bill of Quantities and Price Schedule General Items
BoQ No | predmet / subject | TITLE | Naziv | UNIT | AMOUNT in Euro excluding taxes
(a) | (b) | (c) |  | ( d) | (e)
1 |  | Contractor’s temporary installations and facilities including fences. | Privremene instalacije i objekti izvođača, uključujući i gradilišnu ogradu. | lump sum | 0
2 |  | Installation site office for the Supervisor | Organizovanje kancelarije za supervizora | lump sum | 0
3 |  | Supply and installation of the General construction work information board, banners and posters | Nabavka i montaža gradilišne table za opšte građevinske radove, banera i postera. | lump sum | 0
4 |  | Supply and installation/placement of permanent plaque | Nabavka i ugradnja informativne (donatorske) table. | lump sum | 0
5 |  | Preparation of the Contractor drawings, As-build Design and Operation and Maintence Manuals | Priprema i izrada projekta izvedenog stanja, kao i priučnika za rad i održavanje objekta. | lump sum | 0
6 |  | Topographical survey on site | Snimanje terena za potrebe građenja | lump sum | 0
7 |  | Providing instruitons to school staff in relation to the handling and use of built-in equipment | Pružanje instrukcija školskom osoblju u vezi sa rukovanjem i korišćenjem ugrađene opreme | lump sum | 0
8 |  | Environmental Management Plan & other plans (WMP, HSP) | Plan upravljanja okolinom i drugi planovi (WMP, HSP) | lump sum | 0
0 |  | SUBTOTAL GENERAL ITEMS | Podtotal Opste stavke |  | 0

## 1.1. Arh građ. -ARCH
Program obrazovanja Crne Gore/ Education program of Montenegro
Predmjer - Izgradnja nove OŠ "Vladimir Nazor"/ Bill of Quantity - Construction of the new Elementary School "Vladimir Nazor" ARHITEKTURA SA GRAĐEVINOM / ARCHITECTURE WITH STRUCTURE
br/ No | predmet / subject | NASLOV | DESCRIPTION | mj.jedinica/ unit | pred.cijena u eurima/ unit price € | Količina / Quantity | Cijena u eurima (bez PDV-a) / Amount in € (excl VAT)
(a) | (b) | (c) |  | ( d ) | (e) | (f) | (g=e*f)
1.1. |  | ARHITEKTONSKO GRAĐEVINSKI RADOVI | ARCHITECTURAL CONSTRUCTION WORKS
|  | PREDMJER I PREDRAČUN ARHITEKTONSKO GRAĐEVINSKIH RADOVA | BILL OF QUANTITY ARCHITECTURAL CONSTRUCTION WORKS
I. |  | PRIPREMNI RADOVI | PREPARATION WORKS
1. |  | Ograđivanje i organizacija gradilišta, uklanjanje drveća predviđenog za uklanjanje elaboratom pejzažne arhitekture, uklanjanje stubova za struju sa izmiještanjem kablova na potrebnu poziciju, obezbjeđenje neophodnih energetskih priključaka, dobijanje dozvola, saglasnosti, plaćanje svih neophodnih taksi i naknada za nesmetano otpočinjanje radova. Organizacija privremene deponije i drugi pripremni radovi koji idu na teret izvođača. Prije početka radova izvođač radova će obaviti sve potrebne pripreme za normalno i pravilno izvršenje radova. | Install temporary fencing and organization of construction site, removal of trees classified for removal by study of landscape design, removal of electricity poles with relocation of cables to the required position, provision of necessary power connections, obtaining permits, consents, payment of all necessary fees and charges for the easy start of works. The organization of the temporary landfill and other preparatory works are the responsibility of the Contractor. Before starting the works, the Contractor will provide all the necessary preparations for the normal and proper execution of the works. | pauš/ LS |  | 1 | 0
2. |  | Uklanjanje zemlje i temelja porušene škole ispod pojasa bivših paviljona, mašinskim putem. Cijena obuhvata rušenje, uklanjanje i utovar, odvoz i istovar sa gradilišta na gradsku deponiju. Očekivana dubina temelja 1.5m. | Removal of soil and foundations of the demolished school starting from the former pavilions, by machine. The price includes demolition, removal and loading, transportation and unloading from the construction site to the city landfill. Expected foundation depth 1.5m. | m2 |  | 1150 | 0
3. |  | Uklanjanje postojećeg krova na fiskulturnoj sali. Cijena obuhvata uklanjanje i utovar, odvoz i istovar sa gradilišta na gradsku deponiju. Oznaka u projektu R3.0. | Removal of the existing roof on the gymnasium. The price includes removal and loading, transportation and unloading from the construction site to the city landfill. Index in the project is R3.0 . | m2 |  | 466.2 | 0
4. |  | Uklanjanje postojeće bravarije na fiskulturnoj sali. Cijena obuhvata uklanjanje i utovar, odvoz i istovar sa gradilišta na gradsku deponiju. Oznaka u projektu SF14, SF15. | Removal of the existing locksmithing on the gymnasium. The price includes removal and loading, transportation and unloading from the construction site to the city landfill. Index in the project is SF14, SF15. | kom/ pcs |  | 8 | 0
5. |  | Uklanjanje postojećih dvokrilnih vrata u fiskulturnoj sali. Cijena obuhvata uklanjanje i utovar, odvoz i istovar sa gradilišta na gradsku deponiju. Oznaka u projektu D13. | Removal of the existing double doors in the gymnasium. The price includes removal and loading, transportation and unloading from the construction site to the city landfill. Index in project D13. | kom/ pcs |  | 1 | 0
6. |  | Uklanjanje postojećeg parketa u fiskulturnoj sali. Cijena obuhvata uklanjanje i utovar, odvoz i istovar sa gradilišta na gradsku deponiju. Oznaka u projektu F1.1. | Removal of the existing parquet in the gymnasium. The price includes removal and loading, transportation and unloading from the construction site to the city landfill. Index in the project F1.1. | m2 |  | 448 | 0
I. |  | PRIPREMNI RADOVI | PREPARATION WORKS |  |  | Ukupno/ Total | 0
II. |  | ZEMLJANI RADOVI | EARTHWORKS
|  | Iskop | Excavation
7. |  | Skidanje humusnog dijela zemlje, mašinskim putem u zoni ispod objekata. Iskop izvesti do dubine od 20cm od površine terena. Upotrebljiv humus prosijati i odvojiti na gradilišnu deponiju za buduću upotrebu. Cijena obuhvata uklanjanje, prosijavanje i skladištenje u okviru gradilišne deponije. | Removal of the humus part of the earth by machine in the area under the facility. Excavate to a depth of 20 cm from the ground surface. Sieve the usable humus and separate it at the construction site dump for future use. The price includes removal, screening and storage within the construction site landfill. | m3 |  | 928 | 0
8. |  | Široki iskop zemlje mašinskim putem, u tlu II do III kategorije za izradu temelja i podruma škole. Iskopani materijal se odlaže na gradilištu i služi za nasipanje temelja i nasipe za saobraćajnice. Obračun izvedenih radova se vrši na osnovu stvarno iskopanih količina materijala u tlu. Za obračun količina iskopanog materijala priznaju se dimenzije osnove temelja uvećane za po 0.60 m sa svake strane, širine temeljnih traka i temeljnih greda uvećane za po 0.30 m sa svake strane, te nagibi 1:1 bočnih strana iskopa čija je visina iznad 2 m. Iskop izvesti prema projektu i datim kotama. Bočne strane pravilno odsjeći a dno nivelisati. U cijenu po m³ iskopanog samoniklog materijala uključeni su troškovi iskopa materijala, kao i odlaganje i deponovanje šljunkovito-pjeskovitog materijala na gradilištu koji se može koristiti za nasipanje temelja, saobraćajnica ili za druge potrebe prilikom izvođenja radova. Ukoliko se prilikom iskopa u zemlji pojave instalacije, ostaci objekata ili slično, uklanjanje istih do potrebne dubine pada na teret izvođača radova. | Wide excavation of the earth by machine, in soil of category II to III for the foundation and basement of the school. The excavated material is deposited on the construction site and is used for filling foundations and road embankments. Calculation of the performed works is done on the basis of the actual excavated quantities of material in the soil. For the calculation of the amount of excavated material, the dimensions of the base of the foundation increased by 0.60 m on each side, the width of the foundation strips and foundation beams increased by 0.30 m on each side, and the 1:1 slopes of the sides of the excavation whose height is above 2 m are recognized. Carry out the excavation according to the project and given elevations. Cut the sides properly and level the bottom. The price per m³ of excavated self-sprouting material includes the costs of excavating the material, as well as the disposal and depositing of gravel-sand material on the construction site that can be used for filling foundations, roadways or for other needs during the execution of works. If installations, remains of buildings or the like appear in the ground during excavation, removing them to the required depth is the responsibility of the contractor. | m3 |  | 8470 | 0
9. |  | Široki iskop zemlje mašinskim putem, u tlu II do III kategorije za izradu stepeništa i tribina uz podrum. Iskopani materijal se odlaže na gradilištu i služi za nasipanje temelja i nasipe za saobraćajnice. Obračun izvedenih radova se vrši na osnovu stvarno iskopanih količina materijala u tlu. Iskop izvesti prema projektu i datim kotama. Bočne strane pravilno odsjeći a dno nivelisati. U cijenu po m³ iskopanog samoniklog materijala uključeni su troškovi iskopa materijala, kao i odlaganje i deponovanje šljunkovito-pjeskovitog materijala na gradilištu koji se može koristiti za nasipanje temelja, saobraćajnica ili za druge potrebe prilikom izvođenja radova. | Wide excavation of the earth by machine, in soil of category II to III for the construction of stairs and tribunes next to the basement. The excavated material is deposited on the construction site and is used for filling foundations and road embankments. Calculation of the performed works is done on the basis of the actual excavated quantities of material in the soil. Performthe excavation in accordance with to the project and given elevations. Cut the sides properly and level the bottom. The price per m³ of excavated self-sprouting material includes the costs of excavating the material, as well as the disposal and depositing of gravel-sand material on the construction site that can be used for filling foundations, roadways or for other needs during the execution of works. | m3 |  | 472 | 0
|  | Nasipanje zemlje | Backfilling
10. |  | Ostvariti minimalni modul stišljivosti od 80 MPa. Teren oko objekta isplanirati i pripremiti za dalje radove. Obračun količina vrši se na osnovu stvarno izvedenih radova na nasipanju. U cijenu po m³ nasipa uključeni su troškovi: dovoza odloženog šljunkovito-pjeskovitog materijala iz iskopa, nasipanje, nabijanje i valjanje materijala u slojevima. Za nasipanje koristiti zemlju deponovanu prilikom iskopa. | Backfilling and tamping of crushed earth around foundations, buried walls and under floor slabs. Fill the soil in layers of a maximum of 30 cm, moisten with water, compact with a vibro roller to the required compaction, roll and level according to the project. Achieve a minimum compressibility modulus of 80 MPa. The terrain around the facillity should be planned and prepared for further work. The calculation of the quantities is based on the actual filling works. The price per m³ of embankment are included the costs of: bringing the deposited gravel-sand material from the excavation, filling, tamping and rolling the material in layers. For filling, use the earth deposited during excavation. | m3 |  | 3342 | 0
11. |  | Utovar, odvoz i istovar viška zemlje sa gradilišta na gradsku deponiju. Obračun materijala po m³ u rastresitom stanju. U cijenu ulazi angažovanje sve neophodne mehanizacije u potpunom izvršenju navedene pozicije. | Loading, transportation and unloading of excess soil from the construction site to the city landfill. Calculation of material per m³ in a loose soil. The price includes the hiring of all the necessary machinery for the complete execution of the above position | m3 |  | 6528 | 0
|  | Razastiranje šljunka | Gravel spreading:
12. |  | Nabavka, prevoz, nasipanje, razastiranje i nabijanje tamponskog sloja šljunka, debljine 30cm, ispod temelja i podne ploče škole. Tamponski sloj šljunka nasuti u slojevima, nabiti i nivelisati po projektu sa tolerancijom po visini +/- 1cm. | Procurement, transportation, filling, spreading and tamping of a buffer layer of gravel, 30 cm thick, under the foundation and floor slab of the school. The buffer layer of gravel is poured in layers, compacted and leveled according to the project with allowed height tolerance of +/- 1cm. | m3 |  | 897 | 0
|  | Kameni obluci uz objekat | Stone pebbles next to the object:
13. |  | Nabavka, prevoz, nasipanje, razastiranje i nabijanje kamenih oblutaka bijele boje preko nabijene zemlje na koju se postavlja sloj tucanika oko škole. Obračun po m³ oblutaka. | Procurement, transportation, filling, spreading and tamping of white stone pebbles over the compacted earth on which a layer of tampons is placed around the school. Calculation per m³ of pebbles. | m3 |  | 10.42 | 0
II. |  | ZEMLJANI RADOVI | EARTHWORKS |  |  | Ukupno/Total | 0
III. |  | BETONSKI I ARMIRANO-BETONSKI RADOVI | CONCRETE AND REINFORCED CONCRETE WORKS
14. |  | Izrada armirano-betonskih temelja prema projektu. Temelje armirati po projektu, detaljima i statičkom proračunu. Beton ugraditi i njegovati po propisima. | Construction of reinforced concrete foundations in accordance to the project. Reinforce the foundations in accordance to the project, details and static calculation. Install and maintain concrete according to regulations.
|  | Temelji samci i trake (Škola MB C30/37) | Foundation singles and strips | m3 |  | 645.98 | 0
|  | Temeljne grede i zidovi (Škola MB C30/37) | Foundation beams and walls | m3 |  | 138.41 | 0
|  | Temelji potpornih zidova ispod tribina (Škola MB C30/37) | The foundations of the supporting walls under the stands | m3 |  | 38.68 | 0
15. |  | Izrada armirano-betonskih spoljašnjih i unutrašnih zidova i platana debljine d=30cm, d=25cm i d=20cm, od betona marke MB C30/37 u dvostranoj glatkoj oplati. Zidove i platna armirati po projektu, detaljima i statičkom proračunu. Prilikom betoniranja ugraditi potrebne ankere i vezne elemente u fasadnim zidovima. Beton ugraditi i njegovati po propisima. | Construction of of reinforced concrete external and internal walls thickness d=30cm, d=25cm and d=20cm from concrete class C30/37 in double-sided smooth formwork. Reinforced walls and panels according to the design, details and static calculation. Install the necessary anchors and connecting elements in the facade walls during concreting. Install and maintain concrete according to regulations
|  | Zidovi podruma | Basement walls | m3 |  | 244.75 | 0
|  | Zidovi prizemlja | Ground floor walls | m3 |  | 285.44 | 0
|  | Zidovi I sprata | The walls of the first floor | m3 |  | 180.47 | 0
16. |  | Izrada armirano-betonskih atičnih zidova i zidova krovne lanterne po projektu od betona marke MB C30/37. Izraditi oplatu sa podupiračima i zidove armirati po projektu, detaljima i statičkom proračunu. Beton ugraditi i njegovati po propisima. | Construction of the reinforced concrete attic walls and roof lantern walls according to the project from concrete class C30/37. Create the formwork with supports and reinforce the walls according to the project, in details and static calculation. Install and maintain concrete in accordance with regulations. | m3 |  | 29.34 | 0
17. |  | Izrada armirano-betonskih stubova, od betona marke MB C30/37 u glatkoj oplati. Stubove armirati po projektu, detaljima i statičkom proračunu. Beton ugraditi i njegovati po propisima. | Construction of reinforced concrete columns, made of C30/37 concrete in smooth formwork. Reinforce the columns according to the project, details and static calculation. Install and maintain concrete in accordance with regulations
|  | Stubovi temelja | Pillars of foundation | m3 |  | 4.47 | 0
|  | Stubovi podruma | Basement pillars | m3 |  | 23.83 | 0
|  | Stubovi prizemlja | Pillars of the ground floor | m3 |  | 51.51 | 0
|  | Stubovi I sprata | Pillars of the first floor | m3 |  | 53.6 | 0
|  | Stubovi krovne lanterne | Pillars of the roof lantern | m3 |  | 9.08 | 0
18. |  | Izrada armirano-betonskih greda, presjeka prema projektu, od betona marke MB C30/37. Izraditi glatku oplatu sa podupiračima i grede armirati po projektu, detaljima i statičkom proračunu. Beton ugraditi i njegovati po propisima. | Construction of reinforced concrete beams, sections according to the project, from C30/37 concrete class. Create smooth formwork with supports and reinforce the beams according to the project, details and static calculation. Install and maintain concrete in accordance with regulations
|  | Grede podruma | Basement beams | m3 |  | 57.71 | 0
|  | Grede prizemlja | Ground floor beams | m3 |  | 118.23 | 0
|  | Grede I sprata | First floor beams | m3 |  | 120.1 | 0
|  | Grede krovne lanterne | Roof lantern beams | m3 |  | 60.54 | 0
19. |  | Izrada armirano-betonske podne ploče, debljine d=15 cm, preko sloja podložnog šljunka, u svemu prema projektu. Beton ugraditi i njegovati po propisima. | Construction of reinforced concrete floor slab, thickness d=15 cm, over a layer of underlying gravel, in all respects according to the project. Install and maintain concrete in accordance to regulations
|  | Škola podrum | School basement | m2 |  | 1401.36 | 0
|  | Škola prizemlje | School ground floor | m2 |  | 922.05 | 0
20. |  | Izrada armirano-betonske međuspratne pune ploče, debljine d=20 cm od betona marke MB C30/37. Izraditi oplatu sa podupiračima i ploče armirati po projektu, detaljima i statičkom proračunu. Beton ugraditi i njegovati po propisima. | Construction of reinforced concrete slab between floors, thickness d=20 cm, made of C30/37 concrete class. Perform of the formwork with supports and reinforcement according to the design, details and static calculation. Install and maintain concrete in accordance to regulations.
|  | Ploča iznad podruma | The slab above the basement floor | m2 |  | 1274.06 | 0
|  | Ploča iznad prizemlja | The slab above the ground floor | m2 |  | 1827.63 | 0
|  | Ploča iznad I sprata | The slab above the first floor | m2 |  | 1523.59 | 0
|  | Ploča iznad krovne lanterne | The slabl above the roof lantern | m2 |  | 504.96 | 0
21. |  | Izrada armirano-betonske kose pune ploče u dijelu brisoleja na prizemlju, debljine d=15 cm od betona marke MB C30/37. Izraditi oplatu sa podupiračima i ploče armirati po projektu, detaljima i statičkom proračunu. Beton ugraditi i njegovati po propisima. | Construction of reinforced-concrete inclined full slab in the part of sun-blinds on the ground floor, thickness d=15 cm from C30/37 concrete class. Make formwork with supports and reinforcement of the slabs according to the project, details and static calculation. Install and maintain concrete in accordance with regulations | m2 |  | 216 | 0
22. |  | Izrada armirano-betonske ploče na školi iznad brisoleja, kao podloge za oluk, debljine d=15 cm od betona marke MB C30/37. Izraditi oplatu sa podupiračima i ploče armirati po projektu, detaljima i statičkom proračunu. Beton ugraditi i njegovati po propisima. | Construction of reinforced concrete slab on the school above the sun-blinds, as a base for the gutter, thickness d=15 cm from C30/37 concrete class. Make formwork with supports and reinforcement of the slabs according to the project, details and static calculation. Install and maintain concrete in accordance with regulations | m2 |  | 200.38 | 0
23. |  | Izrada armirano-betonskih stepenica sa međupodestima, kosim stepenišnim pločama i stepenicima, betonom marke MB C30/37. Izraditi oplatu sa podupiračima i ploče armirati po projektu, detaljima i statičkom proračunu. Beton ugraditi i njegovati po propisima. U cijenu ulaze i oplata, podupirači i pomoćna skela. | Construction of reinforced concrete stairs with intermediate landings, inclined stair plates and steps, concrete brand MB C30/37. Make the formwork with supports and reinforcement according to the project, details and static calculation. Install and maintain concrete in accordance with regulations. The price includes formwork, supports and auxiliary scaffolding
|  | Dvokrake stepenice u školi između podruma i prizemlja, i prizemlja i prvog sprata, debljina ploče 15cm, 3 komada | Construction of two-legged stairs in the school between the basement and the ground floor, and the ground floor and the first floor, plate thickness 15 cm, 3 pieces | m3 |  | 15.8 | 0
|  | Jednokrake stepenice između prizemlja i trga, debljina ploče 15cm, 2 komada | One-step stairs between the ground floor and the square, plate thickness 15cm, 2 pieces | m3 |  | 3.06 | 0
24. |  | Izrada armirano-betonskih tribina u podrumu i prizemlju škole u produžetku stepenica, betonom marke MB C30/37. Izraditi oplatu sa podupiračima i ploče i gažišta tribina armirati po projektu, detaljima i statičkom proračunu. Beton ugraditi i njegovati po propisima. U cijenu ulaze i oplata, podupirači i pomoćna skela. Tribine, gazište debljine ploče 15cm i čelo visine 35cm. | Construction of reinforced concrete grandstands in the basement and ground floor of the school in the extension of the stairs, with C30/37 concrete class. Make the formwork with supports, reinforcement and stairs of thegrandstands according to the project, details and static calculation. Install and maintain concrete according to regulations. The price includes formwork, supports and auxiliary scaffolding. | m3 |  | 6.52 | 0
25. |  | Izrada armirano-betonskih tribina u nivou podruma škole sa dva stepeništa i potpornim zidovima, betonom marke MB C30/37. Izraditi oplatu sa podupiračima i ploče i gažišta tribina armirati po projektu, detaljima i statičkom proračunu. Beton ugraditi i njegovati po propisima. U cijenu ulaze i oplata, podupirači i pomoćna skela. Obračun po m³ sve kompletno, 2 komada | Construction of reinforced concrete grandstands in the basement level of the school with two staircases and supporting walls, concrete class is C30/37. Make formwork with supports, reinforcement and stairs of the grandstands according to the project, details and static calculation. Install and maintain concrete according to regulations. The price includes formwork, supports and auxiliary scaffolding." | m3 |  | 120.28 | 0
26. |  | Izrada betonskog libažnog sloja debljine d=5 cm ispod temelja samaca, temeljnih ploča, temeljnih traka i podnih ploča. | Construction of a concrete sub-layer with a thickness of d=5 cm under the foundations of single beams, foundation slabs, foundation strips and floor slabs. | m2 |  | 2625.56 | 0
27. |  | Izrada sloja zaštitnog betona sa rabic mrežicom debljine d=4 cm ispod temelja samaca, temeljnih ploča, temeljnih traka i podnih ploča. | Construction of protective concrete layer with the rabic mesh, thickness d=4 cm under the foundations of the singles, foundation slabs, foundation strips and floor slabs. | m2 |  | 2625.56 | 0
28. |  | Izrada nearmirane sokle debljine 10cm, na spoju krova i oluka. | Creation of unreinforced beam 10 cm thick, at the junction of the roof and the gutter | m3 |  | 4.78 | 0
29. |  | Izrada nearmirane betonske rampe na bočnim evakuacionim izlazima škole. | Construction of non-reinforced concrete ramp at the side evacuation exits of the school. | m3 |  | 9.48 | 0
III. |  | BETONSKI I ARMIRANO-BETONSKI RADOVI | CONCRETE AND REINFORCED CONCRETE WORKS |  |  | Ukupno | 0
IV. |  | ARMIRAČKI RADOVI | REINFORCEMENT WORKS
30. |  | Količina armature data je aproksimativno prema količinama betona, a za obračun sa Investitorom služiće planovi i specifikacije armature, kao i građevinska knjiga. | Procurement, transport, straightening, cutting, cleaning, bending and installation of reinforcement in the formwork in accordance with the details from the static calculation and valid PTP for this type of work. The amount of reinforcement is given approximately according to the amount of concrete,and the plans and specifications of the armature, as well as the construction book, will be used for settlement with the Investor.
|  | Šipke B500B | Bars B500B | kg |  | 391187 | 0
|  | Mreže B500A/B500B | mesh B500A/B500B | kg |  | 93666 | 0
IV. |  | ARMIRAČKI RADOVI | REINFORCEMENT WORKS: |  |  | Ukupno | 0
V. |  | ZIDARSKI RADOVI | MASONRY WORKS
|  | Zidanje | Masonry
31. |  | Zidanje unutrašnjih pregradnih zidova giter blokovima dimenzija 19x19x25 cm u produžnom malteru. Debljina zida je 19 i 25 cm. Blokove prije ugradnje kvasiti vodom. Po završenom zidanju spojnice očistiti do dubine 2 cm. | Masonry of interior walls with giter blocks of 19x19x25cm incement-lime mortar ratio 1:2:6. thickness of walls are d=19 and 25cm. Wet the blocks before installation. After finishing masonry, clean the joints to a depth of 2 cm.
|  | Zidovi u podrumu | Walls in the basement | m3 |  | 66.03 | 0
|  | Zidovi na prizemlju | Walls on the ground floor | m3 |  | 156.34 | 0
|  | Zidovi na prvom spratu | Walls on the first floor | m3 |  | 195.33 | 0
|  | Zidovi na lanterni | Walls on the lantern | m3 |  | 11.84 | 0
32. |  | Zidanje unutrašnjih pregradnih zidova giter blokovima dimenzija 19x19x12 cm u produžnom malteru. Debljina zida je 12 cm. Blokove prije ugradnje kvasiti vodom. Po završenom zidanju spojnice očistiti do dubine 2 cm. | Masonry of interior walls with giter blocks of 19x19x12cm incement-lime mortar ratio 1:2:6. thickness of walls are d=12cm. Wet the blocks before installation. After finishing masonry, clean the joints to a depth of 2 cm.
|  | Zidovi u podrumu | Walls in the basement | m2 |  | 35.14 | 0
|  | Zidovi na prizemlju | Walls on the ground floor | m2 |  | 261.75 | 0
|  | Zidovi na prvom spratu | Walls on the first floor | m2 |  | 22.51 | 0
|  | Malterisanje | Mortar
33. |  | Malterisanje unutrašnjih zidnih površina mašinskim produžnim malterom u dvije ruke, debljine u svemu prema projektu i detaljima. Prije malterisanja površine od opeke dobro očistiti i isprskati mlijekom, a betonske površine premazati kontakt betonom. Na uglovima postaviti pocinčane ugaone lajsne. Malter nanijeti preko podloge i narezati radi boljeg prihvatanja drugog sloja. Drugi sloj spraviti sa sitnim i čistim pijeskom, bez primjesa mulja i organskih materija. Perdašiti uz kvašenje i glačanje. Omalterisane površine moraju biti ravne, bez preloma i talasa, a ivice oštre i prave. Malter kvasiti da ne dođe do brzog sušenja i „pregorijevanja“. | Coating of internal wall surfaces with a two-hand mechanical cement-limemortar, thickness according to the project and details. Before coating, the brick surface should be thoroughly cleaned and sprayed with milk, and concrete surfaces should be coated with prymer, intended for this use. Place galvanized corner moldings over the corners. Apply the mortar over the surface and score it for better acceptance of the second layer. Make the second layer with fine and clean sand, without admixture of mud and organic matter. Process surface with wetting. Plastered surfaces must be flat, without breaks and waves, and the edges sharp and straight. Keep the mortar wet to prevent rapid drying and "burning".
|  | Podrum | Basement | m2 |  | 1810.1 | 0
|  | Prizemlje | Ground floor | m2 |  | 2854.81 | 0
|  | Prvi sprat | First floor | m2 |  | 2865 | 0
|  | Krovna lanterna | Roof lantern | m2 |  | 241.32 | 0
34. |  | Malterisanje unutrašnjih zidnih površina koje se oblažu keramičkim pločicama mašinskim cementnim malterom u dvije ruke, debljine u svemu prema projektu i detaljima. Prije malterisanja površine od opeke dobro očistiti i isprskati mlijekom, a betonske površine premazati kontakt betonom. Na uglovima postaviti pocinčane ugaone lajsne. Malter nanijeti preko podloge i narezati radi boljeg prihvatanja drugog sloja. Drugi sloj spraviti sa sitnim i čistim pijeskom, bez primjesa mulja i organskih materija. Perdašiti uz kvašenje i glačanje. Omalterisane površine moraju biti ravne, bez preloma i talasa, a ivice oštre i prave. Malter kvasiti da ne dođe do brzog sušenja i „pregorijevanja“. | Coating of internal wall surfaces, which will befinally coverd with ceramic tiles. Use ''machine'' cement mortar in two hands, thickness in accordance with the project and details. Before plastering, the brick surface should be thoroughly cleaned and sprayed with milk, and concrete surfaces should be coated withprymer for that purpose. Place galvanized corner moldings on the corners. Apply the mortar over thesurface and score it for better acceptance of the second layer. Make the second layer with fine and clean sand, without admixture of mud and organic matter. Prepare layer with occasional wetting. Plastered surfaces must be flat, without breaks and waves, and the edges must be sharp and straight. Keep the mortar wet to prevent rapid drying and "burning".
|  | Podrum | Basement | m2 |  | 147.88 | 0
|  | Prizemlje | Ground floor | m2 |  | 334.86 | 0
|  | Prvi sprat | First floor | m2 |  | 305.61 | 0
35. |  | Malterisanje unutrašnjih plafonskih površina ekonomsko-tehničkih prostorija u podrumu škole, mašinskim produžnim malterom u dvije ruke, debljine u svemu prema projektu i detaljima. Prije malterisanja betonske površine premazati kontakt betonom. Na uglovima postaviti pocinčane ugaone lajsne. Malter nanijeti preko podloge i narezati radi boljeg prihvatanja drugog sloja. Drugi sloj spraviti sa sitnim i čistim pijeskom, bez primjesa mulja i organskih materija. Perdašiti uz kvašenje i glačanje. Omalterisane površine moraju biti ravne, bez preloma i talasa, a ivice oštre i prave. Malter kvasiti da ne dođe do brzog sušenja i „pregorijevanja“. | Coating of the interior ceiling surfacesin the economic and technical rooms at the basement of the school, with mechanical cement-lime mortar, in two layer. thickness in accordance with the project and details. Before plastering the concrete surface, coat the parymer intended for this purpose. Place galvanized corner moldings on the corners. Apply the mortar on thesurfaces and score it as to give a good bonding of the second layer. Make the second layer with fine and clean sand, without admixture of mud and organic matter. Plastered surfaces must be flat, without breaks and waves, and the edges must be sharp and straight. Keep the mortar wet to prevent rapid drying and "burning". | m2 |  | 253.13 | 0
|  | Cementni estrih | Cement screed (estrih)
36. |  | Izrada rabiciranog cementnog estriha kao podloge za dalju obradu podova, u svemu prema projektu i detaljima. | Perform of cement screed, reinforced by ''rabic'' mesh. Cement screed is the base for further floor treatment, according to the project and details.
|  | d=5 cm | d=5 cm | m2 |  | 2668.1 | 0
|  | d=4.5 cm | d=4.5 cm | m2 |  | 1385.64 | 0
|  | d=4 cm | d=4 cm | m2 |  | 909.95 | 0
|  | d=3.5 cm | d=3.5 cm | m2 |  | 185.31 | 0
37. |  | Izrada sloja za pad od rabiciranog cementnog estriha, na krovu i krovnoj lanterni u dijelu horizontalnih oluka škole u svemu prema projektu i detaljima. Debljina estriha 4-7cm. | Perform of the failed layer of the cement screed, reinforced by ''rabic''mesh, on the roof and the roof, lantern, and the part of the horizontal gutters of the school, according to the project and details. Screed thickness 4-7cm. | m2 |  | 2128.1 | 0
V. |  | ZIDARSKI RADOVI | MASONRY WORKS |  |  | Ukupno | 0
VI. |  | KROVOPOKRIVAČKI I LIMARSKI RADOVI | ROOFING AND SHEET METAL WORKS
38. |  | Montaža krovnih termoizolacionih sendvič panela debljine 10cm. Panele montirati prateći pad, u pravcu atika-horizontalnih oluka, u jednom komadu, šrafljenjem za čelične rožnjače. Montažu vršiti u svemu prema detaljima iz projekta i uputstvima proizvođača. Sve mjere uzeti na licu mjesta. U cijenu je uračunat sav potreban materijal, prevoz i ugradnja. Boja panela: Bianco-grigio ili ekvivalentno | Placing of roof thermal insulation sandwich panels with a thickness of 10 cm. Mount the panels following the fall, in the direction of the attic-horizontal gutters, in one piece, by screwing for steel cornices. Assembly should be carried out in accordance with the project details and the manufacturer's instructions. All measures taken on the spot. The price includes all necessary materials, transportation and installation. Panel color: Bianco-grigio or equivalent | m2 |  | 466.2 | 0
39. |  | Montaža limenih opšivki na atici - krovu fiskulturne sale. Montažu vršiti u svemu prema detaljima iz projekta i uputstvima proizvođača. Sve mjere uzeti na licu mjesta. U cijenu je uračunat sav potreban materijal, prevoz i ugradnja. Boja limene opšivke RAL 7036. Razvijena širina limene opšivke 40cm | Installation of sheet metal flashing on the attic - the roof of the Sports Hall. Assembly should be carried out in accordance with the details of thedesign and the manufacturer's instructions. All measures take on the spot. The price includes all necessary materials, transport and installation. The color of the sheet matal is RAL 7036. The developed width of the sheet metal flashing is 40 cm. | m1 |  | 91.3 | 0
40. |  | Montaža horizontalnih limenih oluka na krovu sale. Montažu vršiti u svemu prema detaljima iz projekta i uputstvima proizvođača. Sve mjere uzeti na licu mjesta. U cijenu je uračunat sav potreban materijal, prevoz i ugradnja. Boja limenog oluka RAL 7036 U cijenu pozicije ulazi i izrada nove hidroizolacije na cementnoj bazi ispod oluka, eventualno izrada slojeva za pad, odnosno uklanjanje postojeće hidroizolacije ispod oluka ukoliko postoji. Razvijena širina limenih oluka 75cm | Preparation and installation of horizontal sheet metal gutters on the Sport Hall roof. Assembly should be carried out in accordance with the details of thedesign and the manufacturer's instructions. All measures are to take on the spot. The price includes all necessary materials, transportat and installation. Sheet metal gutter color is RAL 7036. The price of the position includes the performing of new waterproofing on the cement base under the gutter, performing of falled cement screed, if it necessary, removal of the existing waterproofing under the gutter if it exists. The developed width of tin gutters is 75 cm | m1 |  | 56 | 0
VI. |  | KROVOPOKRIVAČKI I LIMARSKI RADOVI | ROOFING AND SHEET METAL WORKS |  |  | Ukupno | 0
VII. |  | IZOLATERSKI RADOVI | INSULATION WORKS
|  | Hidroizolacija | Waterproofing layer
41. |  | Nabavka i izrada vertikalne drenažne membrane uz ukopane podrumske zidove objekta kao zaštite XPS-a i hidroizolacije. Tip: SIKA DRAIN S 400g/m2 ili ekvivalentno | Procurement and production of a vertical drainage membrane along the buried basement walls of the building as XPS protection and waterproofing. Type: SIKA DRAIN S 400g/m2 or equivalent
|  | Škola_podrumski dio | School _ Basement floor slab | m2 |  | 921.16 | 0
|  | Škola_bez podruma | Shool_ without basement | m2 |  | 443.89 | 0
42. |  | Nabavka i izrada horizontalne hidroizolacije po podnoj ploči objekta. Izolaciju podići uz obodne zidove min. 30cm, što ulazi u jediničnu cijenu pozicije. U poziciju su uračunati i svi potrebni holkeri, kao u detaljima. Tip: SIKALASTIC 1K ili ekvivalentno | Procurement and production of horizontal waterproofing on the floor slab of the building. Raise the insulation along the perimeter walls min. 30 cm, which is included in the unit price of the position. All the necessary holkers are included in the position, as in the details. Type: SIKALASTIC 1K or equivalent
|  | Podna ploča podruma | Basement floor slab | m2 |  | 1301.48 | 0
|  | Podna ploča prizemlja | Ground floor slab | m2 |  | 859.05 | 0
43. |  | Nabavka i izrada horizontalne hidroizolacije u sanitarnim čvorovima u objektu i na oba trijema. Izolaciju podići uz obodne zidove min. 30cm, što ulazi u jediničnu cijenu pozicije. U poziciju su uračunati i svi potrebni holkeri, kao u detaljima. Tip: SIKALASTIC 1K ili ekvivalentno | Procurement and perform of horizontal waterproofing layer in sanitary rooms in the building and on both porches. Raise the insulation along the perimeter walls min. 30 cm, which is included in the unit price of the position. All the necessary holkers are included in the position, as in the details. Type: SIKALASTIC 1K or equivalent
|  | Podrum | Basement | m2 |  | 23.54 | 0
|  | Prizemlje | Ground floor | m2 |  | 184.77 | 0
|  | Prvi sprat | First floor | m2 |  | 56.76 | 0
44. |  | Nabavka i izrada horizontalne poliuretanske hidroizolacije sa kvarcnim posipom na krovu. Izolaciju podići uz atiku, što ulazi u jediničnu cijenu. U poziciju su uračunati i svi potrebni premazi, holkeri, prajmer, filc i kvarc, kao u detaljima. Tip: SIKALASTIC 614 ili ekvivalentno | Procurement and production of horizontal polyurethane waterproofing with quartz sprinkles on the roof. Raise the insulation with the attic, which is included in the unit price. The position includes all necessary coatings, holkers, primer, felt and quartz, as in the details. Type: SIKALASTIC 614 or equivalent
|  | Krov škole | School roof | m2 |  | 1813.55 | 0
|  | Krovna lanterna škole | School roof lantern | m2 |  | 606.74 | 0
45. |  | Nabavka i izrada horizontalne poliuretanske hidroizolacije na krovu - obloga primarne hidroizolacije na horizontalnim olucima. Izolaciju podići uz atiku. U poziciju su uračunati i svi potrebni holkeri, kao u detaljima. Tip: SIKALASTIC 701 ili ekvivalentno | Procurement and production of horizontal polyurethane waterproofing on the roof - lining of primary waterproofing on horizontal gutters. Raise the insulation along the attic. All the necessary holkers are included in the position, as in the details. Type: SIKALASTIC 701 or equivalent
|  | Krov škole | School roof | m2 |  | 207.88 | 0
|  | Krovna lanterna škole | School roof lantern | m2 |  | 111.62 | 0
46. |  | Nabavka i izrada primarne hidroizolacije (PVC membrane) uz ukopane zidove u podrumu, ispod temeljnih stopa, temeljnih greda, podne ploče objekta, kao i pozicije ispod zida zavjese. Izolaciju podići uz obodne zidove minimum 30cm, što ulazi u jediničnu cijenu pozicije. U poziciju su uračunati i svi potrebni holkeri, kao i zaštita hidroizolacije geotekstilom kao u detaljima. Tip: SIKA PLAN WP 1100-20 HL ili ekvivalentno | Procurement and production of primary waterproofing (PVC membrane) along the underground walls in the basement, under the footings, foundation beams, floor slabs of the building, as well as the position under the curtain wall. Raise the insulation along the perimeter walls by a minimum of 30 cm, which is included in the unit price of the position. The position includes all the necessary holkers, as well as waterproofing protection with geotextile as in the details. Type: SIKA PLAN WP 1100-20 HL or equivalent
|  | Škola podrumski dio vertikalna hidroizolacija | School basement part _ vertical waterproofing | m2 |  | 1390.47 | 0
|  | Škola bez podruma vertikalna hidroizolacija | School without the basement_ vertical waterproofing | m2 |  | 947.85 | 0
|  | Zid ispod zid zavjese vertikalna hidroizolacija | The wall under the curtain wall _ vertical waterproofing | m2 |  | 247.07 | 0
|  | Škola podrumski dio horizontalna hidroizolacija | School basement part _horizontal waterproofing | m2 |  | 1949.26 | 0
|  | Škola bez podruma horizontalna hidroizolacija | School without basement_ horizontal waterproofing | m2 |  | 1437.69 | 0
|  | Termoizolacija | Thermal insulation
47. |  | Nabavka i ugradnja horizontalne termoizolacije u sklopu podova, d=4 cm. Tip: URSA XPS-N-III-I ili ekvivalentno | Procurement and installation of horizontal thermal insulation as part of the floors, d=4 cm. Type: URSA XPS-N-III-I or equivalent
|  | Podrum | Basement | m2 |  | 1327.67 | 0
|  | Prizemlje | Ground floor | m2 |  | 1987.11 | 0
|  | I sprat | First floor | m2 |  | 1897.86 | 0
48. |  | Nabavka i ugradnja horizontalne termoizolacije u sklopu krova škole, minimalna debljina je 25cm a maksimalna 34cm. Sa gornje strane štititi PE folijom, a u krovu predvidjeti i parnu branu sa donje strane termoizolacije. U cijenu pozicije ulazi i parna brana i PE folija. Tip: URSA XPS-N-III-L + SARNAVAP 5000 E SA FR ili ekvivalentno | Procurement and installation of horizontal thermal insulation as part of the school roof, the minimum thickness is 25cm and the maximum is 34cm. On the upper side, protect with PE foil, and in the roof, provide a vapour barrier on the lower side of the thermal insulation. The price of the position includes a vapor barrier and PE foil. Type: URSA XPS-N-III-L + SARNAVAP 5000 E SA FR or equivalent | m2 |  | 1584.01 | 0
49. |  | Nabavka i ugradnja horizontalne termoizolacije u sklopu krova krovne lanterne škole, minimalna debljina je 20cm a maksimalna 28cm. Sa gornje strane štititi PE folijom, a u krovu predvidjeti i parnu branu sa donje strane termoizolacije. U cijenu pozicije ulazi i parna brana i PE folija. Tip: URSA XPS-N-III-L + SARNAVAP 5000 E SA FR ili ekvivalentno | Procurement and installation of horizontal thermal insulation as part of the roof lantern school roof, the minimum thickness is 20cm and the maximum is 28cm. On the upper side, protect with PE foil, and in the roof, provide a vapor barrier on the lower side of the thermal insulation. The price of the position includes a vapor barrier and PE foil. Type: URSA XPS-N-III-L + SARNAVAP 5000 E SA FR or equivalent. | m2 |  | 466.78 | 0
50. |  | Nabavka i ugradnja vertikalne termoizolacije u dijelu ukopanih zidova u podrumu i kao ispune dilatacije škole, d=10, 8, 3cm. Tip: URSA XPS-N-III-L ili ekvivalentno | Procurement and installation of vertical thermal insulation in the part of theunderground walls in the basement and as a filling for expansion joint of the school, d=10, 8, 3cm. Type: URSA XPS-N-III-L or equivalent
|  | d=10cm | d=10cm | m2 |  | 136.11 | 0
|  | d=8cm | d=8cm | m2 |  | 475 | 0
|  | d=3cm | d=3cm | m2 |  | 323.71 | 0
VII. |  | IZOLATERSKI RADOVI | INSULATION WORKS |  |  | Ukupno | 0
VIII. |  | GIPSARSKI RADOVI | PLASTERING WORKS
51. |  | Izrada spuštenog plafona od akustičnih gips-kartonskih ploča 12,5 mm, na metalnoj potkonstrukciji. U cijenu uračunata i radna skela. Oznaka u projektu C2.2. | Production of a suspended ceiling from acoustic plasterboard panels of 12.5 mm, on a metal substructure. The price includes scaffolding. The design lebel C2.2.
|  | Podrum | Basement | m2 |  | 895.63 | 0
|  | Prizemlje | Ground floor | m2 |  | 1743.19 | 0
|  | I sprat | First floor | m2 |  | 1547.21 | 0
|  | Krovna lanterna | Roof lantern | m2 |  | 457.24 | 0
52. |  | Izrada spuštenog plafona od vlagootpornih gips-kartonskih ploča 12,5 mm, na metalnoj potkonstrukciji u sanitarnim prostorijama. U cijenu uračunata i radna skela. Oznaka u projektu C2.1. | Construction of a suspended ceiling from moisture-resistant gypsum-cardboard boards of 12.5 mm, on a metal substructure in sanitary rooms. The price includes scaffolding. The design lebel C2.1. | m2 |  | 3.6 | 0
53. |  | Obloge debljine 5 cm od dvostrukih običnih gips-kartonskih ploča. Oznaka u projektu W1.2. | Linings of 5 cm thickness made of double ordinary gypsum-cardboard boards. Project lebel W1.2. | m2 |  | 220.52 | 0
54. |  | Obloge debljine 7.5 cm od dvostrukih vlagootpornih gips-kartonskih ploča. Oznaka u projektu W1.1. i W1.3. | Linings of 7.5 cm thickness made of double moisture-resistant gypsum-cardboard boards. Project lebel W1.1. and W1.3. | m2 |  | 180.85 | 0
VIII. |  | GIPSARSKI RADOVI | PLASTERING WORKS |  |  | Ukupno | 0
IX. |  | STOLARSKI I BRAVARSKI RADOVI | JOINERY AND LOCKSMITHING WORKS
|  | Unutrašnja bravarija | Internal joinery
55. |  | Unutrašnja jednokrilna vrata sa staklom unutar krila. Krilo vrata se sastoji od rama od masiva, sa ispunom od ekstrudirane iverice, okantovano sa sve četiri strane, obloženo furniranim medijapanom, ukupne debljine min 42 mm. Štok se sastoji od masivne lamelirane ploče od tvrđe vrste drveta ili sendviča od kompozitnih ploča sa ojačanjem od šper ploče u samom štoku da bi dobili konstrukciju koja garantuje čvrsto vezivanje šarki u štoku. Štok je obostrano obložen tankim medijapanom koji obezbjeđuje dimenzionalnu stabilnost , ukupne debljine min 40 mm. Okov: brodska šarka 4 kom , brava sa cilindrom sa minimum 3 ključa za zaklučavanjem, diht guma q-lon 3113 ili ekvivalentno. Ručka: inox Proizvođač je dužan da definiše način ugradnje radioničkim crtežima na koje je obavezan da dobije saglasnost naručioca,odnosno projektanta. Pri izradi i montaži pozicije poštovati sve preporuke od strane proizvođača profila. Izvođač je dužan dostaviti atestnu dokumentaciju usaglašenu sa EN standardima. Obračun po komadu kompletno izvedene pozicije. | Interior single-leaf glazed door. The door leaf consists of a frame made of solid wood, filled with extruded chipboard, edged on all four sides, and covered with veneered mediapan; the thickness is min. 42 mm. The door frame is made of a solid laminated board of harder wood or a sandwich of composite boards with plywood reinforcement on the positions of the hinges in the frame. The frame is coated on both sides with a thin mediapan, which provides dimensional stability; the thickness of the frame is at least 40 mm. Hardware: marine hinge 4 pcs., cylinder lock with a minimum of 3 keys, sealing rubber q-lon 3113 or equivalent. Handle: stainless steel. The manufacturer must define the installation manufacturer method with workshop drawings and have to obtain consent from the client and the designer. During the works, follow all the recommendations of the manufacturer. The contractor have to submit certificates by EN standards. Calculation per piece of a completely executed position
|  | Oznaka u projektu: D01 - 100 x 230 cm | Item symbol in the design: D01 - 100 x 230 cm | kom/ pcs |  | 30 | 0
56. |  | Unutrašnja jednokrilna vrata škole. Krilo vrata se sastoji od rama od masiva, sa ispunom od ekstrudirane iverice, okantovano sa sve četiri strane, obloženo furniranim medijapanom, ukupne debljine min 42 mm. Štok se sastoji od masivne lamelirane ploče od tvrđe vrste drveta ili sendviča od kompozitnih ploča sa ojačanjem od šper ploče u samom štoku da bi dobili konstrukciju koja garantuje čvrsto vezivanje šarki u štoku. Štok je obostrano obložen tankim medijapanom koji obezbjeđuje dimenzionalnu stabilnost , ukupne debljine min 40 mm. Okov: brodska šarka 4 kom , brava sa cilindrom sa minimum 3 ključa za zaklučavanjem, diht guma q-lon 3113 ili ekvivalentno. Ručka: inox Proizvođač je dužan da definiše način ugradnje radioničkim crtežima na koje je obavezan da dobije saglasnost naručioca,odnosno projektanta. Pri izradi i montaži pozicije poštovati sve preporuke od strane proizvođača profila. Izvođač je dužan dostaviti atestnu dokumentaciju usaglašenu sa EN standardima. Obračun po komadu kompletno izvedene pozicije. | The internal single door of the school. The door leaf consists of a frame made of solid wood, filled with extruded chipboard, edged on all four sides, covered with veneered median, the total thickness of min. 42 mm. The door frame is made from a solid laminated board of solid wood or a sandwich of composite boards with plywood reinforcement on places of the hinges. The frame is coated on both sides with a thin median, which provides dimensional stability; the total thickness is at least 40 mm. Hardware: marine hinge 4 pcs., cylinder lock with a min of 3 keys, sealing rubber q-lon 3113 or equivalent. Handle: stainless steel. The manufacturer have to define the installation method with drawings approved by the client and the designer. During the works, follow all the recommendations of the manufacturer. The contractor have to submit certificates by EN standards . Calculation per piece of a completely executed position.
|  | Oznaka u projektu: D02 - 100 x 230 cm | Project item label: D02 - 100 x 230 cm | kom/pcs |  | 8 | 0
|  | Oznaka u projektu: D03 - 100 x 230 cm | Project item label: D03 - 100 x 230 cm | kom/pcs |  | 5 | 0
|  | Oznaka u projektu: D03V - 100 x 230 cm | Projectitem label: D03V - 100 x 230 cm | kom/pcs |  | 2 | 0
|  | Oznaka u projektu: D04 - 90 x 230 cm | Project item label: D04 - 90 x 230 cm | kom/pcs |  | 11 | 0
|  | Oznaka u projektu: D04V - 90 x 230 cm | Project item label: D04V - 90 x 230 cm | kom/pcs |  | 11 | 0
|  | Oznaka u projektu: D05V - 90 x 230 cm | Projectitem label: D05V - 90 x 230 cm | kom/pcs |  | 4 | 0
|  | Oznaka u projektu: D06V - 90 x 230 cm | Project item label: D06V - 90 x 230 cm | kom/pcs |  | 4 | 0
|  | Oznaka u projektu: D07V - 80 x 230 cm | Project item label: D07V - 80 x 230 cm | kom/pcs |  | 3 | 0
|  | Oznaka u projektu: D08 - 75 x 230 cm | Project item label: D08 - 75 x 230 cm | kom/pcs |  | 6 | 0
57. |  | Unutrašnja dvokrilna vrata škole. Krilo vrata se sastoji od rama od masiva, sa ispunom od ekstrudirane iverice, okantovano sa sve četiri strane, obloženo furniranim medijapanom, ukupne debljine min 42 mm. Štok se sastoji od masivne lamelirane ploče od tvrđe vrste drveta ili sendviča od kompozitnih ploča sa ojačanjem od šper ploče u samom štoku da bi dobili konstrukciju koja garantuje čvrsto vezivanje šarki u štoku. Štok je obostrano obložen tankim medijapanom koji obezbjeđuje dimenzionalnu stabilnost , ukupne debljine min 40 mm. Okov: brodska šarka 4 kom , brava sa cilindrom sa minimum 3 ključa za zaklučavanjem, diht guma q-lon 3113 ili ekvivalentno. Ručka: inox Proizvođač je dužan da definiše način ugradnje radioničkim crtežima na koje je obavezan da dobije saglasnost naručioca,odnosno projektanta. Pri izradi i montaži pozicije poštovati sve preporuke od strane proizvođača profila. Izvođač je dužan dostaviti atestnu dokumentaciju usaglašenu sa EN standardima. Obračun po komadu kompletno izvedene pozicije. | Internal double doors of the school. The door leaf consists of a frame made of solid wood, filled with extruded chipboard, edged on all four sides, covered with veneered mediapan, the thickness of min. 42 mm. The door frame is made of a solid laminated board of a more rigid type of wood or a sandwich of composite boards with plywood reinforcement that guarantees a tight binding of the hinges in the frame. The frame is coated on both sides with a thin mediapan, which provides dimensional stability, and the thickness of the frame is at least 40 mm. Hardware: marine hinge 4 pcs., cylinder lock with a minimum of 3 keys, sealing rubber q-lon 3113 or equivalent. Handle: stainless steel. The manufacturer must define the installation method with workshop drawings and obtain the consent of the client and the designer. During the works, follow all the recommendations of the manufacturer. The contractor must submit certificates in accordance with EN standards. Calculation per piece of a completely executed position.
|  | Oznaka u projektu: D10V - 200 x 230 cm | Project item label: D10V - 200 x 230 cm | kom |  | 2 | 0
|  | Oznaka u projektu: D11 - 180 x 230 cm | Project item label: D11 - 180 x 230 cm | kom/ pcs |  | 2 | 0
58. |  | Unutrašnja staklena pregrada u školi sa jednokrilnim vratima. Krilo vrata se sastoji od rama od masiva, sa ispunom od ekstrudirane iverice, okantovano sa sve četiri strane, obloženo furniranim medijapanom, ukupne debljine min 42 mm. Štok se sastoji od masivne lamelirane ploče od tvrđe vrste drveta ili sendviča od kompozitnih ploča sa ojačanjem od šper ploče u samom štoku da bi dobili konstrukciju koja garantuje čvrsto vezivanje šarki u štoku. Štok je obostrano obložen tankim medijapanom koji obezbjeđuje dimenzionalnu stabilnost , ukupne debljine min 40 mm. Okov: brodska šarka 4 kom , brava sa cilindrom sa minimum 3 ključa za zaklučavanjem, diht guma q-lon 3113 ili ekvivalentno. Ručka: inox Proizvođač je dužan da definiše način ugradnje radioničkim crtežima na koje je obavezan da dobije saglasnost naručioca,odnosno projektanta. Pri izradi i montaži pozicije poštovati sve preporuke od strane proizvođača profila. Izvođač je dužan dostaviti atestnu dokumentaciju usaglašenu sa EN standardima. Obračun po komadu kompletno izvedene pozicije. | Internal glazed partition in the school with a single door. The door leaf consists of a frame made of solid wood, filled with extruded chipboard, edged on all four sides, and covered with veneered mediapan; the thickness is min. 42 mm. The door frame is made from a solid laminated board of a more rigid type of wood or a sandwich of composite boards with plywood reinforcement that guarantees the tight binding of the hinges in the frame. The frame is coated on both sides with a thin median, which provides dimensional stability; the thickness of the frame is at least 40 mm. Hardware: marine hinge 4 pcs., cylinder lock with a minimum of 3 keys, sealing rubber q-lon 3113 or equivalent. Handle: stainless steel. The manufacturer must define the installation method with workshop drawings, and obtain the client's and the designer's consent. During the works, follow all the recommendations of the manufacturer. The contractor have to submit certificates in accordance with EN standards. Calculation per piece of a completely executed position
|  | Oznaka u projektu: D09V - 300 x 230 cm | Project item label: D09V - 300 x 230 cm | kom/ pcs |  | 1 | 0
59. |  | Protivpožarna jednokrilna vrata škole. Štok vrata je izrađen od 2 vertikalna i jednog horizontalnog profila od pocinkovanog čeličnog lima debljine 1,5mm Sa unutrašnje strane štoka je postavljena termoekspandirajuća traka. Po obimu štoka je ugrađena protivpožarna diht guma Na štoku se nalaze 3 šarke od kojih je jedna sa oprugom za samozatvaranje vrata Krilo vrata je izrađeno od dve table čeličnog lima debljine 0,8mm. Ispunu krila čine dvije protivpožarne gipsane ploče debljine 12,5mm između kojih se nalazi tvrdo presovana kamena vuna debljine 35mm Ukupna debljina krila je 62mm Protivpožarna čelična brava i cilindar Protivpožarne čelična kvaka presvučena PVC-om u crnoj boji sa 3 rezervna ključa, i sa odgovarajućim sertifikatom. Obračun po komadu kompletno izvedene pozicije. | Fireproof single-leaf doors of the school. The door frame is made of 2 vertical and one horizontal profile made of galvanized steel sheet with the thickness of 1.5 mm. A thermo-expanding tape is placed on the inside of the frame. A fire-resistant sealing rubber is installed around the frame. The door is installed with 3 hinges on the frame, one of which has the spring for self-closing the door. The door leaf is made of two 0.8 mm thick steel sheets. The leaf is filled with two 12.5mm fire-resistant plasterboards, between which there is 35 mm thick hard-pressed stone wool. The thickness of the leaf is 62mm. Fireproof steel lock and cylinder The fire-resistant steel handle is coated with PVC in black with 3 spare keys and the appropriate certificate. Calculation per piece of a completely executed position.
|  | Oznaka u projektu: D04f - 90 x 230 cm | Project item label: D04f - 90 x 230 cm | kom/ pcs |  | 6 | 0
60. |  | Protivpožarna dvokrilna vrata škole. Štok vrata je izrađen od 2 vertikalna i jednog horizontalnog profila od pocinkovanog čeličnog lima debljine 1,5mm Sa unutrašnje strane štoka je postavljena termoekspandirajuća traka. Po obimu štoka je ugrađena protivpožarna diht guma. Na štoku se nalaze 3 šarke od kojih je jedna sa oprugom za samozatvaranje vrata Krilo vrata je izrađeno od dve table čeličnog lima debljine 0,8mm. Ispunu krila čine dvije protivpožarne gipsane ploče debljine 12,5mm između kojih se nalazi tvrdo presovana kamena vuna debljine 35mm Ukupna debljina krila je 62mm Protivpožarna čelična brava i cilindar Protivpožarne čelična kvaka presvučena PVC-om u crnoj boji sa 3 rezervna ključa, i sa odgovarajućim sertifikatom. Obračun po komadu kompletno izvedene pozicije. | Fireproof two-leave doors of the school. The door frame is made of 2 vertical and one horizontal profile made of galvanized steel sheet with the thickness of 1.5 mm. A thermo-expanding tape is placed on the inside of the frame. A fire-resistant sealing rubber is installed around the frame. The door is installed with 3 hinges on the frame, one of which has the spring for self-closing the door. The door leaves are made of two 0.8 mm thick steel sheets. The leaves are filled with two 12.5mm fire-resistant plasterboards, between which there is 35 mm thick hard-pressed stone wool. The thickness of the leaves are 62mm. Fireproof steel lock and cylinder The fire-resistant steel handle is coated with PVC in black with 3 spare keys and the appropriate certificate. Calculation per piece of a completely executed position.
|  | Oznaka u projektu: D11f - 180 x 230 cm | Project item label: D11f - 180 x 230 cm | kom/ pcs |  | 8 | 0
61. |  | Unutrašnja dvokrilna vrata sale. Krilo vrata se sastoji od rama od masiva, sa ispunom od ekstrudirane iverice, okantovano sa sve četiri strane, obloženo furniranim medijapanom, ukupne debljine min 42 mm. Štok se sastoji od masivne lamelirane ploče od tvrđe vrste drveta ili sendviča od kompozitnih ploča sa ojačanjem od šper ploče u samom štoku da bi dobili konstrukciju koja garantuje čvrsto vezivanje šarki u štoku. Štok je obostrano obložen tankim medijapanom koji obezbjeđuje dimenzionalnu stabilnost , ukupne debljine min 40 mm. Okov: brodska šarka 4 kom , brava sa cilindrom sa minimum 3 ključa za zaklučavanjem, diht guma q-lon 3113 ili ekvivalentno. Ručka: inox Proizvođač je dužan da definiše način ugradnje radioničkim crtežima na koje je obavezan da dobije saglasnost naručioca,odnosno projektanta. Pri izradi i montaži pozicije poštovati sve preporuke od strane proizvođača profila. Izvođač je dužan dostaviti atestnu dokumentaciju usaglašenu sa EN standardima. Obračun po komadu kompletno izvedene pozicije. | Internal double doors of the hall. The door leaf consists of a frame made of solid wood, filled with extruded chipboard, edged on all four sides, covered with veneered mediapan; the total thickness is min. 42 mm. The door frame is made from a solid laminated board of a harder type of wood or a sandwich of composite boards with plywood reinforcement , that guarantees a tight binding of the hinges in the frame. The frame is coated on both sides with thin mediapan, which provides dimensional stability,; the total thickness of frame is at least 40 mm Hardware: marine hinge 4 pcs., cylinder lock with a minimum of 3 keys, sealing rubber q-lon 3113 or equivalent. Handle: stainless steel. The manufacturer must define the method of installation with drawings, and provide the client's and the designer's consent. Follow all the recommendations of the profile manufacturer during the works. The Contractor must submit standards in accordance with EN standards. Calculation per piece of a complitelly finished position.
|  | Oznaka u projektu: D13 - 150 x 200 cm | Project item label: D13 - 150 x 200 cm | kom |  | 1 | 0
|  | Spoljašnja bravarija | Exterior joinery
62. |  | Vrata tipa ALUMIL S67 ili ekvivalentno, u svemu prema šemi. Okvir je od aluminijumskih profila sa termoprekidom S67510. Okvir je pričvršćen za zid ankerima (vijcima) na dovoljnom broju mjesta po svim stranama bez mogućnosti pomjeranja. Svi spojevi okvira i zida sa vanjske strane obrađeni su Illbruck ME501 ili ekvivalentnim trakama, a na naliježućoj strani profila na zid Illbruck Trioplex, ili ekvivalentnim trakama. Maksimalna toplotna provodljivost profila je Uf= 1,1-2,6 W/m²K. Krila su od aluminijumskih profila sa termoprekidom S67936. Krila su zastakljena termoizolacionim staklom tipa 6 /16/ 4 (26 mm Ugmax= 0.9 W/m²K, PSI 0,044 W/m²K), svjetlosne transmisije min 27% i solarnog faktora max 28%. - Zaptivke između stakla i alumijuma su od visokokvalitetnih EPDM guma iz sistema otpornih na atmosferske uticaje. Zaptivanje između štoka i krila je obezbijeđeno kroz tri dihtunga. Vrata su predviđena za izlaz na krov iz krovne lanterne. | Door ALUMIL S67 type or equivalent, in accordance with the scheme. The frame is made of aluminum profiles with thermal break S67510. The frame is fixed to the wall with anchors (screws) sufficiently number on places on all sides to prevent movement. All joints of the frame and the wall on the outside are treated with Illbruck ME501 or equivalent strips, and on the adjacent side of profile on the wall Illbruck Trioplex, or equvalente tapes. The maximum thermal conductivity of the profile is Uf= 1.1-2.6 W/m²K. The wings are made of aluminum profiles with thermal break S67936. The wings are glazed with heat-insulating glass type 6 /16/ 4(26 mm) Ugmax= 0.9 W/m²K, PSI 0.044 W/m²K), light transmission min 27% and solar factor max 28%. - Seals between glass and aluminum are made of high-quality EPDM rubber from a system resistant to atmospheric influences. Sealing between frame and wing is ensured by three gaskets. The door is intended for exit to the roof from the roof lantern.
|  | Oznaka u projektu: D12 - 120 x 155 cm | Project item label: D12 - 120 x 155 cm | kom |  | 2 | 0
63. |  | Prozor tipa ALUMIL S67 ili ekvivalentno. Okvir je od aluminijumskih profila sa termoprekidom S67510. Okvir je pričvršćen za zid ankerima (vijcima) na dovoljnom broju mjesta po svim stranama bez mogućnosti pomjeranja. Svi spojevi okvira i zida sa vanjske strane obrađeni su Illbruck ME501 ili ekvivalentnim trakama, a na naliježućoj strani profila na zid Illbruck Trioplex, ili ekvivalentnim trakama. Maksimalna toplotna provodljivost profila je Uf= 1,1-2,6 W/m²K. Krila su od aluminijumskih profila sa termoprekidom S67936. Krila su zastakljena termoizolacionim staklom tipa 6 /16/ 4 (26 mm Ugmax= 0.9 W/m²K, PSI 0,044 W/m²K), svjetlosne transmisije min 27% i solarnog faktora max 28%. - Zaptivke između stakla i alumijuma su od visokokvalitetnih EPDM guma iz sistema otpornih na atmosferske uticaje. Zaptivanje između štoka i krila je obezbijeđeno kroz tri dihtunga. - Sistem okova uključuje elemente protiv pogrešnog rukovanja kao i limitere otvaranja krila, u svemu prema specifikaciji dobavljača. Okov omogućuje komforno rukovanje prilikom bravljenja i odbravljivanja. Obrada unutra : antracit RAL 7016 Obrada spolja: antracit RAL 7016 | Window is made from Alumil S67's aluminium profiles or equivalent. The frame is made of aluminum profiles with thermal break S67510. The frame is fixed to the wall with anchors (screws) sufficiently number on places over all sides to prevent movement. All joints of the frame and the wall on the outside are treated with Illbruck ME501 tapes or equivalent, and on to the adjacent side of the profile on the Illbruck Trioplex wall strips, or equivalent . The maximum thermal conductivity of the profile is Uf= 1.1-2.6 W/m²K. The wings are made of aluminum profiles with thermal break S67936. The wings are glazed with heat-insulating glass type 6 /16/ 4 (26 mm, Ugmax= 0.9 W/m²K, PSI 0.044 W/m²K), light transmission min 27% and solar factor max 28%. - Seals between glass and aluminum are made of high-quality EPDM rubber from a system resistant to atmospheric influences. Sealing between frame and wing is ensured by three gaskets. - According to the supplier's specifications, the hardware system includes anti-spoil elements and wing opening limiters. The hardware enables comfortable handling when locking and unlocking.
|  | Oznaka u projektu: W01 - 145 x 145 cm. | Project item label: W01 - 145 x 145 cm. | kom/ pcs |  | 1 | 0
|  | Zid zavjese | Curtain wall
64. |  | FASADNA KONSTRUKCIJA "ZID ZAVJESA" od fasadnih aluminijumskih profila u sistemu ALUMIL SMARTIA M7 ili ekvivalentno. - Okovi testirani u sistemu profila, sa otvaranjem prema datoj šemi. - Otpornost okova na koroziju klasa 5. Pozicija je zastakljena dvostrukim termoizolacionim staklom tipa 6 mm + 16 mm+ 6 mm, Ug=1,0 W/m2K / tipa 8 mm + 12 mm+ 8 mm, Ug=1,1 W/m2K sa pvc distancerom za staklo sa poboljšanim termičkim karakteristikama. Potrebnu debljinu stakla dimenzionisati u zavisnosti od veličine otvora, izloženosti uticajima i traženoj zvučnoj izolaciji.. Maksimalna debljina stakla 54 mm. Završna obrada aluminijuma je fabrička plastifikacija, u boji RAL 7016 (anthracite grey) sa unutrašnje i spoljašnje strane. | FACADE CONSTRUCTION "CURTAIN WALL" Made of facade aluminum profiles in the ALUMIL SMARTIA M7 system or equivalent. - Fittings tested in the profile system, with openings in accordance with the given scheme. - Corrosion resistance of fittings class 5. The position is glazed with double thermal insulating glass type 6 mm + 16 mm+ 6 mm, Ug=1.0 W/m2K / type 8 mm + 12 mm+ 8 mm, Ug=1.1 W/m2K with thePVC spacer for glass with improved thermal characteristics . Dimension the required glass thickness depending on the size of the opening, exposure to influences and required sound insulation. Maximum glass thickness 54 mm. Aluminum finishes treatment is factory plastic coating, in the color RAL 7016 (anthracite gray) both, inside and outside.
|  | Oznaka u projektu: SF01 - 754 x 320cm. | Project item label: SF01 - 754 x 320cm. | kom/ pcs |  | 3 | 0
|  | Oznaka u projektu: SF01a - 744 x 320cm. | Project item label: SF01a - 744 x 320cm. | kom/ pcs |  | 1 | 0
|  | Oznaka u projektu: SF07 - 227 x 325cm. | Project item label: SF07 - 227 x 325cm. | kom/ pcs |  | 4 | 0
|  | Oznaka u projektu: SF08 - 226 x 325cm. | Project item label: SF08 - 226 x 325cm. | kom/ pcs |  | 2 | 0
|  | Oznaka u projektu: SF09 - 1562 x 350cm. | Project item label: SF09 - 1562 x 350cm. | kom/ pcs |  | 2 | 0
|  | Oznaka u projektu: SF10L - 490 x 95cm. | Project item label: SF10L - 490 x 95cm. | kom/ pcs |  | 2 | 0
|  | Oznaka u projektu: SF10D - 490 x 95cm. | Project item label: SF10D - 490 x 95cm. | kom/ pcs |  | 2 | 0
|  | Oznaka u projektu: SF11 - 754 x 95cm. | Project item label: SF11 - 754 x 95cm. | kom/ pcs |  | 4 | 0
|  | Oznaka u projektu: SF12 - 714 x 95cm. | Project item label: SF12 - 714 x 95cm. | kom/ pcs |  | 2 | 0
|  | Oznaka u projektu: SF13 - 744 x 95cm. | Project item label: SF13 - 744 x 95cm. | kom/ pcs |  | 2 | 0
65. |  | FASADNA KONSTRUKCIJA "ZID ZAVJESA" od fasadnih aluminijumskih profila u sistemu ALUMIL SMARTIA M7 ili ekvivalentno. - Okovi testirani u sistemu profila, sa otvaranjem prema datoj šemi. - Otpornost okova na koroziju klasa 5. Pozicija je zastakljena dvostrukim termoizolacionim staklom tipa 6 mm + 16 mm+ 6 mm, Ug=1,0 W/m2K / tipa 8 mm + 12 mm+ 8 mm, Ug=1,1 W/m2K sa pvc distancerom za staklo sa poboljšanim termičkim karakteristikama. Potrebnu debljinu stakla dimenzionisati u zavisnosti od veličine otvora, izloženosti uticajima i traženoj zvučnoj izolaciji.. Maksimalna debljina stakla 54 mm. Puna netransparentna polja zid zavjese sastoje se od termoizolacionog panela sa spoljnom oblogom od jednoslojnog emajliranog stakla, ispunom od tvrdo presovane termoizolacije i unutrašnjom oblogom od aluminijumskog lima debljine 2mm, u boji i završnoj obradi profila. Panel mora dihtovati po čitavom obodu polja. Završna obrada aluminijuma je fabrička plastifikacija, u boji RAL 7016 (anthracite grey) sa unutrašnje i spoljašnje strane. | FACADE CONSTRUCTION "CURTAIN WALL" made from facade aluminum profiles in the ALUMIL SMARTIA M7 system or equivalent. Fittings tested in the profile system, with opening according to the given scheme. - Corrosion resistance of fittings class 5. The position is glazed with double thermal insulating glass type 6 mm + 16 mm+ 6 mm, Ug=1.0 W/m2K / type 8 mm + 12 mm+ 8 mm, Ug=1.1 W/m2K with the PVC spacer for glass with improved thermal characteristics . Dimensioned the required glass thickness depending on the size of the opening, exposure to influences and required sound insulation. Maximum glass thickness 54 mm. The full non-transparent fields of the curtain wall consist of the thermal insulation panel with an outer coating of single-layer enameled glass, a filling of hard-pressed thermal insulation and an inner coating of aluminum sheet thickness 2mm, in the color and finishing of the profile. The panel must be sealed around the entire perimeter of the position. Aluminum finishes treatment is factory plastic coating, in colour RAL 7016 (anthracite grey) both, inside and outside.strane.
|  | Oznaka u projektu: SF02L - 260 x 720cm. | Project item label: SF02L - 260 x 720cm. | kom/pcs |  | 1 | 0
|  | Oznaka u projektu: SF02d - 260 x 720cm. | Project item label: SF02d - 260 x 720cm. | kom/pcs |  | 1 | 0
|  | Oznaka u projektu: SF03 - 260 x 720cm. | Project item label: SF03 - 260 x 720cm. | kom/pcs |  | 2 | 0
|  | Oznaka u projektu: SF04 - 235 x 640cm. | Project item label: SF04 - 235 x 640cm. | kom/pcs |  | 4 | 0
|  | Oznaka u projektu: SF05 - 227 x 640cm. | Project item label: SF05 - 227 x 640cm. | kom/pcs |  | 32 | 0
|  | Oznaka u projektu: SF06 - 226 x 640cm. | Project item label: SF06 - 226 x 640cm. | kom/pcs |  | 18 | 0
66. |  | FASADNA KONSTRUKCIJA "ZID ZAVJESA" od fasadnih aluminijumskih profila u sistemu ALUMIL SMARTIA M7 ili ekvivalentno na objektu sale. - Okovi testirani u sistemu profila, sa otvaranjem prema datoj šemi. - Otpornost okova na koroziju klasa 5. Pozicija je zastakljena dvostrukim termoizolacionim staklom tipa 8 mm + 12 mm+ 8 mm, Ug=1,1 W/m2K sa pvc distancerom za staklo sa poboljšanim termičkim karakteristikama. Potrebnu debljinu stakla dimenzionisati u zavisnosti od veličine otvora, izloženosti uticajima i traženoj zvučnoj izolaciji.. Maksimalna debljina stakla 54 mm. Panel mora dihtovati po čitavom obodu polja. Završna obrada aluminijuma je fabrička plastifikacija, u boji RAL 7016 (anthracite grey) sa unutrašnje i spoljašnje strane. | FACADE CONSTRUCTION "CURTAIN WALL" made from facade aluminum profiles in the ALUMIL SMARTIA M7 system or equivalent on gzmnasium facility. - Fittings tested in the profile system, with opening according to the given scheme. - Corrosion resistance of fittings class 5. The position is glazed with double thermal insulating glass type 8 mm + 12 mm + 8 mm, Ug=1.1 W/m2K with a PVC spacer for glass with improved thermal characteristics. Dimension the required glass thickness depending on the size of the opening, exposure to influences and required sound insulation. Maximum glass thickness 54 mm. The panel must be sealed around the entire perimeter of the position. Aluminum finishes treatment is factory plastic coating, in colourRAL 7016 (anthracite grey) both, inside and outside.
|  | Oznaka u projektu: SF14 - 675 x 300cm. | Project item label: SF14 - 675 x 300cm. | kom/pcs |  | 4 | 0
67. |  | FASADNA KONSTRUKCIJA "ZID ZAVJESA" od fasadnih aluminijumskih profila u sistemu ALUMIL SMARTIA M7 ili ekvivalentno na objektu sale. - Okovi testirani u sistemu profila, sa otvaranjem prema datoj šemi. - Otpornost okova na koroziju klasa 5. Pozicija je zastakljena dvostrukim termoizolacionim staklom tipa 8 mm + 12 mm+ 8 mm, Ug=1,1 W/m2K sa pvc distancerom za staklo sa poboljšanim termičkim karakteristikama. Potrebnu debljinu stakla dimenzionisati u zavisnosti od veličine otvora, izloženosti uticajima i traženoj zvučnoj izolaciji.. Maksimalna debljina stakla 54 mm. Panel mora dihtovati po čitavom obodu polja. - Brisoleji se sastoje od ekstrudiranih aluminijumskih profila. Lamelice postavljati horizontalno pod uglom od 45° i kačiti na potkonstrukciju preko sistemskih aluminijumskih prihvatnika. Profil je zaštićen procesom plastifikacije u boji po izboru projektanta i investitora. Završna obrada aluminijuma je fabrička plastifikacija, u boji RAL 7016 (anthracite grey) sa unutrašnje i spoljašnje strane. | FACADE CONSTRUCTION "CURTAIN WALL" from facade aluminum profiles in the ALUMIL SMARTIA M7 system or equivalent on the building of the hall. - Fittings tested in the profile system, with opening according to the given scheme. - Corrosion resistance of fittings class 5. The position is glazed with double thermal insulating glass type 8 mm + 12 mm + 8 mm, Ug=1.1 W/m2K with a pvc spacer for glass with improved thermal characteristics. Dimension the required glass thickness depending on the size of the opening, exposure to influences and required sound insulation. Maximum glass thickness 54 mm. The panel must be sealed around the entire perimeter of the position. - Brisolei (shutters) consist of extruded aluminum profiles.Instal the slats horizontally at an angle of 45° and hang them on the substructure by system aluminum holders. The profile is protected by a plasticization process in the color chosen by the designer and investor. Aluminum finishes treatment is factory plastic coating, in colour RAL 7016 (anthracite grey) both, inside and outside. Aluminum finishes treatment is factory plastic coating, in colour boji RAL 7016 (anthracite grey) both, inside and outside.
|  | Oznaka u projektu: SF15 - 675 x 300cm. | Project item label: SF15 - 675 x 300cm. | kom/pcs |  | 4 | 0
|  | Kancelarijske pregrade | Office partitions:
68. |  | Kancelarijske pregrade u dijelu produženog boravka i biblioteke sa medijatekom. Sistem SMARTIA P100 ili sl. je sistem unutrašnjih pregrada od veoma tankih pokrivnih aluminijumskih profila, koji nude širok izbor prednosti, a glavna karakteristika su mogućnosti dizajna, čvrstoća i jednostavnost montaže. Završna obrada: Antracit 7016 Dubina sistema: 70 mm Zvučne izolacija: 48 dB Obračun po komadu kompletno izvedene pozicije. | Office partitions situated in the extended stay section and a library with a media library. SMARTIA P100 system or similar. is a system of internal partitions made of very thin covering aluminum profiles, which offer a wide variety of advantages, the main feature being design possibilities, strength and ease of assembly. Finish: Anthracite 7016 System depth: 70 mm Sound insulation: 48 dB Calculation per piece of the finished position.
|  | Oznaka u projektu: KP01 - 2624 x 318 cm | Projectitem label: KP01 - 2624 x 318 cm | kom/pcs |  | 1 | 0
|  | Oznaka u projektu: KP02 - 244 x 318 cm | Project item label: KP02 - 244 x 318 cm | kom/pcs |  | 2 | 0
|  | Oznaka u projektu: KP03 - 214 x 318 cm | Project item label: KP03 - 214 x 318 cm | kom/pcs |  | 1 | 0
|  | Ograde | Fences
69. |  | Ograda visine 110cm, mjereno od gotovog poda, se sastoji od ravnih čeličnih flahova širine 50mm i debljine 5mm, postavljenih na krajevima, dnu i vrhu ograde, i čeličnih flahova profila ''T'' dužine 20mm, širine 50mm i debljine 5mm kao središnje podjele ograde. Ispuna ograde su mreže istegnutog metala, ravnog profila, koje se pričvršćuju čeličnim vijcima za flahove. Sva polja su jednake širine. Rukohvat je od bezbojno lakiranog masivnog drveta - hrasta, širine 50mm i visine 30mm. Ograda se pričvršćuje za armirano-betonsku ploču pomoću čeličnih vijaka potrebne dužine. Sve spojeve i varove idealno izraditi, očistiti i obrusiti. Prije ugradnje ogradu očistiti, nanijeti impregnaciju i obojiti osnovnom bojom za metal. Završna boja ograde je bijela - RAL 9016. | The fence of 110 cm height, measured from the finished floor, consists of flat steel sheets 50 mm wide and 5 mm thick, placed at the ends, bottom and top of the fence, and "T" profile steel sheets 20 mm long, 50 mm wide and 5 mm thick as central divisions fences. The filling of the fence is nets of stretched metal, with a flat profile, which are attached with steel bolts for flats. All fields are of equal width. The handle is made of colorless lacquered solid wood - oak, width 50mm and height 30mm. The fence is attached to the reinforced concrete slab using steel bolts of the required length. All joints and welds should be ideally made, cleaned and sanded. Before installing the fence, clean it, apply impregnation and paint it with a base paint for metal. The finish color of the fence is white - RAL 9016.
|  | Ograda RL01 - L = 566cm, H =110cm, 6 kom | Fence RL01 - L = 566cm, H =110cm, 6 pcs | m1 |  | 33.96 | 0
|  | Ograda RL02 - L = 405cm, H =110cm, 4 kom | Fence RL02 - L = 405cm, H =110cm, 4 pcs | m1 |  | 16.2 | 0
|  | Ograda RL03 - L = 611cm, H =110 -118 cm, 3 kom | Fence RL03 - L = 611cm, H =110 -118 cm, 3 pcs | m1 |  | 18.33 | 0
|  | Ograda RL04 - L = 611cm, H =110 -118 cm, 3 kom | Fence RL04 - L = 611cm, H =110 -118 cm, 3 pcs | m1 |  | 18.33 | 0
|  | Ograda RL05 - L =3880cm, H =110 cm, 1 kom | Fence RL05 - L =3880cm, H =110 cm, 1 pcs | m1 |  | 38.8 | 0
|  | Ograda RL06 - L =397.5cm, H =75.5cm, 2 kom | Fence RL06 - L =397.5cm, H =75.5cm, 2 pcs | m1 |  | 7.95 | 0
|  | Ograda RL07 - L =215cm, H =110cm, 2 kom | Fence RL07 - L =215cm, H =110cm, 2 pcs | m1 |  | 4.3 | 0
70. |  | Ograda visine 120cm, mjereno od linije gotovog trga, se sastoji od kutijastih čeličnih profila dimenzija 40x20mm, debljine 2mm postavljenih na krajevima, dnu i vrhu ograde, i čeličnih šipki dužine 116cm, dimenzija 20x20mm, debljine 2mm kao središnje podjele ograde. Osovinski raspon čeličnih šipki iznosi 15cm. Sve spojeve i varove idealno izraditi, očistiti i obrusiti. Prije ugradnje ogradu očistiti, nanijeti impregnaciju i obojiti osnovnom bojom za metal. Završna boja kapije je siva - RAL 7035. | The 120 cm high fence, measured from the line of the finished square, consists of box steel profiles with dimensions 40x20 mm, thickness 2 mm placed at the ends, bottom and top of the fence, and steel bars 116 cm long, dimensions 20x20 mm, thickness 2 mm as the central division of the fence. The axial span of the steel bars is 15 cm. All joints and welds should be ideally made, cleaned and sanded. Before installing the fence, clean it, apply impregnation and paint it with a base paint for metal. The final color of the gate is gray - RAL 7035.
|  | Ograda RL08 - L =1002cm, H =120cm, 4kom | Fence RL08 - L =1002cm, H =120cm, 4 pcs | m1 |  | 40.08 | 0
71. |  | Rukohvat visine 120cm, mjereno linije gotovog stepeništa, se sastoji od kutijastog čeličnog profila dimenzija 40x20mm, debljine zida 2mm ukrućenog dovoljnim brojem čeličnih nosača. Sve spojeve i varove idealno izraditi, očistiti i obrusiti. Prije ugradnje ogradu očistiti, nanijeti impregnaciju i obojiti osnovnom bojom za metal. Završna boja rukohvata je siva - RAL 7035. | Handrail height 120 cm, measured along the finished staircase line, consists of a box steel profile with dimensions 40x20 mm, wall thickness 2 mm, stiffened by a sufficient number of steel supports. All joints and welds should be ideally made, cleaned and sanded. Before installation, clean the fence, apply impregnation and paint it with base paint for metal. The final color of the handle is gray - RAL 7035.
|  | Rukohvat RL09 - L = 776cm, H =120cm, 4 kom | Handrail RL09 - L = 776cm, H =120cm, 4 pcs | m1 |  | 31.04 | 0
|  | Sanitarne montažne pregrade | Sanitary mounting partitions:
72. |  | Izrada i montaža sanitarnih pregrada od kompakt-ploča i pratećeg okova. Kompakt-ploče su debljine 13 mm, apsolutno vodopostojane, higijenske, ne trule, postojane na: grebanje, lom i udare, blago hrapave površinske strukture. Plastificirani ili eloksirani aluminijski profil za vrata, dovratnik, sadrži gumenu traku za neutralisanje zvuka pri zatvaranju vrata. Priključak na zid se izvodi sa plastificiranim aluminijskim ''U'' profilom. Prednja strana pregrade sadrži plastificirani aluminijski profil koji je učvršćuje po cijeloj dužini gornje ivice. Na krilima su ugrađene po dvije šarke od plastificiranog metala sa ugrađenom oprugom za samozatvaranje u gornjoj šarki. Šarke su učvršćene na dovratni profil sa po dva vijka od inox-a. Nožice su izrađene od plastificiranih aluminijskih cijevi E6/EV1, sa mogućnošću podešavanja visine do 15 cm. Za pod je nožica pričvršćena preko pločice nogica izrađene od PVC-a, sa 50 mm visokom zaštitnom rozetom iz poliamida. Standardna visina kabina je 220 cm, uključujući nožice. Standardna širina vrata iznosi 65 cm. Sve kabine su opremljene sa po jednom vješalicom za garderobu i odbojnikom za vrata. | Making and installation of sanitary partitions from compact panels and accompanying fittings. Compact panels are 13 mm thick, absolutely waterproof, hygienic, non-rotting, resistant to: scratching, breaking and impacts, slightly rough surface structure. The plasticized or anodized aluminum profile for the door, and the door frame, contains a rubber band to neutralize the sound when the door is closed. The connection to the wall is made with a plasticized aluminum "U" profile. The front side of the partition contains a plasticized aluminum profile that strengthens it along the entire length of the upper edge. Two hinges made of plasticized metal are installed on the wings with a built-in self-closing spring in the upper hinge. The hinges are fixed to the door profile with two stainless steel screws. The legs are made of plasticized aluminum tubes E6/EV1, with the possibility of height adjustment up to 15 cm. The leg is attached to the floor via a leg plate made of PVC, with a 50 mm high protective rosette made of polyamide. The standard height of the cabins is 220 cm, including the legs. The standard door width is 65 cm. All cabins are equipped with one wardrobe hanger and door bumper.
|  | Boja kompakt-ploča biće određena od strane projektanta. Sve mjere uzeti na licu mjesta. Sitna usijecanja i prekrojavanja moguća su na licu mjesta uz odobrenje projektanta ili stručnog nadzora. U cijenu je uračunat sav potreban materijal, prevoz i ugradnja. | The color of the compact panel will be determined by the designer. All measures take on the spot. Small cuts and alterations are possible on site with the approval of the designer or supervisor. The price includes all necessary materials, transportation and installation.
|  | Oznaka u projektu SP01: 354x210+15cm, 4 vrata | Project item label SP01: 354x210+15cm, 4 doors | kom/pcs |  | 4 | 0
|  | Oznaka u projektu SP02: 268x210+15cm, 3 vrata | Project label SP02: 268x210+15cm, 3 doors | kom/pcs |  | 2 | 0
|  | Oznaka u projektu SP03: 30x210+15cm | Project item label SP03: 30x210+15cm | kom/pcs |  | 8 | 0
|  | Oznaka u projektu SP04: 30x105+15cm | Project item label SP04: 30x105+15cm | kom/pcs |  | 8 | 0
|  | Drvene klupice | Wooden coverings:
73. |  | Nabavka, izrada i ugradnja drvenih klupica na tribinama u nastavku stepeništa. Drvene klupice su od punog drveta debljine 5cm, izbačene od spoljnje ivice zida za po 2cm u prostor. Klupice se završno tretiraju sredstvima za drvo koje im obezbjeđuje dugovječnost, i lakiraju bezbojnim lakom. Ugrađuju se na lijepku za drvo. U cijenu ulazi sve gorenavedno u okviru pozicije. Drvene klupice na tribinama 205x91 oznaka u projektu KL1 | Procurement, manufacture and installation of wooden benches on the grandstands in the continuation of the staircase. The wooden benches are made of solid wood 5 cm thick, protruding from the outer edge of the wall by 2 cm into the space. The benches are finally treated with wood products that ensure their longevity, and varnished with colorless varnish. They are installed on wood glue. The price includes everything obovementioned within position. Wooden benches on the grandstands 205x91 marks in the KL1 project | kom/ pcs |  | 2 | 0
IX. |  | STOLARSKI I BRAVARSKI RADOVI | JOINERY AND LOCKSMITHING WORKS |  |  | Ukupno | 0
X. |  | KERAMIČARSKI RADOVI | CERAMIC WORKS
74. |  | Nabavka materijala i oblaganje podova podnim protivkliznim keramičkim pločicama, I klase, laserski rezane, dimenzija 120x120cm u boji i tonu prema usvojenom uzorku. Pločice polagati u sloju lijepka u slogu fuga na fugu sa minimalnom fugom i fugovanjem u boji i tonu po izboru projektanta. U sanitarnim prostorijama pločice polagati u padu prema rešetki u podu od min. 1%. U cijenu je uračunata i izrada sokle od iste keramike, visine 10cm, na mjestima gdje je to potrebno. | Pocurement of materials and covering the floors by slip-resistance ceramic floor tiles, first class quality, laser cut, dimensions 120x120cm in color and tone according to the adopted sample. Install the tiles in a layer of adhesive in a joint-to-joint sequence with minimal grouting and grouting in the color and tone selected by the designer. In the sanitary rooms, the tiles should be laid in a slope towards the grating in the floor of min. 1%. The price also includes the production of a plinth made of the same ceramic, 10 cm high, in places where it is necessary.
|  | Podrum | Basement floor | m2 |  | 505.83 | 0
|  | Prizemlje | Ground floor | m2 |  | 966.49 | 0
|  | I sprat | First Floor | m2 |  | 644.62 | 0
75. |  | Nabavka materijala i oblaganje zidova keramičkim pločicama, I klase, laserski rezane, dimenzija 60x60cm u boji i tonu prema usvojenom uzorku. Svu zidnu keramiku postavljati do visine od min 10cm iznad spuštenog plafona. Pozicija obuhvata potrebne ugaone lajsne. Pločice polagati u sloju lijepka u slogu fuga na fugu sa fugovanjem u boji i tonu po izboru projektanta. | Procurement of materials and covering the walls with ceramic tiles, 1st class quality, laser cut, dimensions 60x60cm in coloUr and tone according to the approved sample. Install all wall ceramics up to a height of at least 10 cm above the suspended ceiling. The position includes the necessary corner moldings. Lay the tiles in a layer of adhesive in a joint-to-joint style with grouting in the color and tone selected by the designer.
|  | Podrum | Basement floor | m2 |  | 162.01 | 0
|  | Prizemlje | Ground floor | m2 |  | 414.65 | 0
|  | I sprat | First Floor | m2 |  | 379.67 | 0
76. |  | Nabavka materijala i oblaganje, podesta, međupodesta, gazišta i čela stepeništa protivkliznim keramičkim pločicama, I klase, laserski rezane, dimenzija 120x120cm u boji i tonu prema usvojenom uzorku. Na spoju gazišta i čela pločice gerovati. Pozicija obuhvata potrebne ugaone lajsne. Pločice polagati u sloju lijepka u slogu fuga na fugu sa fugovanjem u boji i tonu po izboru projektanta. | Procurement of materials and coating, landing, intermediate landing, treads and stair fronts with non-slip ceramic tiles, class I, laser cut, size 120x120cm in colour and tone according to the adopted sample. At the junction of the tread and the front of the stairs, cut the edges of the tiles to an angle of 45°. The position includes the necessary corner mouldings. Lay the tiles in a layer of adhesive in a joint-to-joint style with grouting in the colour and tone selected by the designer.
|  | Podrum 1 stepenište | Basement 1 stairs | m2 |  | 30.45 | 0
|  | Prizemlje 2 stepeništa | Ground floor 2 stairs | m2 |  | 60.9 | 0
|  | Prizemlje 2 stepeništa na trijemovima | Ground floor 2 stairs on the porches | m2 |  | 18.75 | 0
77. |  | Nabavka materijala i oblaganje krova protivkliznim keramičkim pločicama, I klase, laserski rezane, dimenzija 60x60cm u boji i tonu prema usvojenom uzorku. Na spoju gazišta i čela pločice gerovati. Pozicija obuhvata potrebne ugaone lajsne. Pločice polagati u sloju lijepka u slogu fuga na fugu sa fugovanjem u boji i tonu po izboru projektanta. | Procurement of materials and coating of the roof with slip resistant ceramic tiles, first class quality , laser cut, dimensions 60x60cm in color and tone according to the adopted sample. The tread and the face of the tile at the junction are to be adjusted. The position includes the necessary corner moldings. Lay the tiles in a layer of adhesive in a joint-to-joint style with grouting in the color and tone selected by the designer.
|  | Krov škole | School roof | m2 |  | 1632.8 | 0
|  | Lanterna škole | School lantern | m2 |  | 495.1 | 0
X. |  | KERAMIČARSKI RADOVI | CERAMIC WORKS |  |  | Ukupno | 0
XI. |  | PODOPOLAGAČKI RADOVI | FLOORING WORKS
78. |  | Nabavka i ugradnja modularne podne obloge od vinila prozivođača TARKETT ili ekvivalentno, debljine 0,7mm na lijepku, preko pripremljene podloge. Boja i šablon kombinacija po izboru projektanta, u skladu sa projektom, tehničkim opisom i specifikacijom materijala. U poziciju ulazi i cijena sokle. U cijenu su uračunati materijal, prevoz i rad. | Procurement and installation of modular floor covering made of vinyl produced by TARKETT or equivalent, 0.7 mm thick on adhesive, over the prepared substrate. Color and pattern combinations chosen by the designer, in accordance with the project, technical description and material specification. The price of the plinth are also include in the position. The price includes material, transportation and labor.
|  | Prizemlje - matične učionice | Ground floor-primary classroom | m2 |  | 682.81 | 0
|  | Prizemlje - predmetne učionice | Ground floor- subject classroom | m2 |  | 62 | 0
|  | Prizemlje - Specijalizovane učionice (kabineti) | Ground school - Specialized classrooms (cabinets) | m2 |  | 19.6 | 0
|  | Prizemlje - Ostale prostorije | Ground floor - other premises | m2 |  | 240.95 | 0
|  | I sprat - matične učionice | I floor -primary classrooms | m2 |  | 624.37 | 0
|  | I sprat - predmetne učionice | I floor - subject classrooms | m2 |  | 501.85 | 0
|  | I sprat - Specijalizovane učionice (kabineti) | First floorl - Specialized classrooms (cabinets) | m2 |  | 118.88 | 0
|  | I sprat - Ostale prostorije | First floor - Other premises | m2 |  | 0 | 0
79. |  | Nabavka, transport i ugradnja komplet novog drvenog sportskog poda na elastičnoj potkonstrukciji u svemu prema FIBA standardu. Parket mora biti izrađen od punog čistog bukovog drveta minimalne debljine 22mm, fabrički lakiran sa gornje strane daske i zaštićen od UV zraka i lakiran sa donje strane daske. Sportski pod poseduje sistem za nivelaciju putem plastičnih kajli. Podna daska je bukov masiv (puno drvo), debljine 22mm, fabrički lakirana sa gornje i donje strane, dimenzija 3700mm x 129mm. Podna daska se na podkonstrukciju ukucava mašinskim putem. Prosečna visina poda 90mm (minimum 62mm maximum 109mm) Uz ponudu obavezno dostaviti: važeći FIBA sertifikat, važeći IHF sertifikat, EN 14904 standard, katalog / tehnički list ponuđenog sportskog poda, uzorak sportskog poda. | Procurement, transport and installation of a set of new wooden sports floor on an elastic substructure, according to the FIBA standard. The parquet must be made of solid pure beech wood with a minimum thickness of 22 mm, factory varnished on the upper side of the board and protected from UV rays and varnished on the lower side of the board. The sports floor has a leveling system by means of plastic wedges. The floorboard is solid beech (solid wood), 22mm thick, factory varnished on the top and bottom, dimensions 3700mm x 129mm. The floor board is machining into the substructure. Average floor height is 90mm (minimum 62mm maximum 109mm) With the offer following have to be submited: valid FIBA certificate, valid IHF certificate, EN 14904 standard, catalog / technical sheet of the offered sports floor, sports floor sample.
|  | Obračun po m² kompletnog poda (uključujući dvodjelnu ventilirajuću drvenu lajsnu i obilježavanje centralnih terena za rukomet, košarku i odbojku linijama širine 5cm u skladu sa propozicijama takmičenja.) | Calculation per m² of the complete floor (including two-part ventilated wooden molding and marking the central courts for handball, basketball and volleyball with 5cm wide lines in accordance with the competition's propositions.) | m2 |  | 448 | 0
80. |  | Izrada dvokomponentnog epoksidnog poda u podrumu škole i na stepeništima i tribinama u parteru. Pod se izvodi u sljedećim koracima: Priprema betonske podloge mašinskim frezanjem i sačmarenjem. Izvodi se zbog odstranjivanja površinski slabih djelova sa komplet čišćenjem i usisavanjem, do prionljivosti podne obloge za podlogu min. 1,5 N/mm2. - Izrada izravnjavajućeg - nosećeg sloja i podnog sistema po sljedećem opisu: 1. Priprema i ugradnja epoksidne SN veze za konstruktivna spajanja. 2. Izrada sloja za izravnavanje sa popunjavanjem eventualnih oštećenja u betonu 3. Izrada završnog epoksidnog poda 4. Trajna impregnacija podnog sistema zaštitnom penetracionom formacijom. Cijena obuhvata izradu svih navedenih slojeva i dovođenje noseće betonske podloge u stanje za izradu epoksidnog poda. Epoksidni pod izvesti u žutoj boji RAL 1023. | Production of a two-component epoxy floor in the basement of the school and on the stairs and stands on the ground floor. These are the steps of performing the floor works: -Preparation of the concrete base by machine milling and shot blasting.It is carried out due to the removal of superficially weak parts with complete cleaning and vacuuming, until good adhesion of the floor covering to the substrate is min. 1.5 N/mm2. Creation of leveling - bearing layer and floor system according to the following description: 1. Preparation and installation of epoxy MV connection for constructive connections. 2.Creation of a leveling layer with the filling of possible damages in the concrete 3. Creation of the final epoxy floor 4. Permanent impregnation of the floor system with a protective penetration formation. The price includes the production of all the mentioned layers and bringing the supporting concrete base to the condition for the production of the epoxy floor. Epoxy floor make in yellow color RAL 1023.
|  | Podrum škole: Hol, biblioteka, produženi boravak, garderobe, multimedijska učionica | Basemnet: Hol, library, extension school stay, dressingkrooms, multimedia classroom. | m2 |  | 687.73 | 0
|  | Tribine, zidovi i stepeništa partera u nivou podruma | Tribunes, walls and grandstastands of the ground floor at the basement level | m2 |  | 562.96 | 0
81. |  | Nabavka i ugradnja aluminijumskih prelaznih lajsni na sastavu dva poda i na prekidima postavljanja podova ispod vrata. Lajsne ugraditi u svemu prema uputstvima proizvođača, a uz saglasnost sa projektantom ili nadzornim organom. | Procurement and installation of aluminum transitional moldings on the composition of the two floors and on the interruptions of the installation of floors under the door. Install the moldings all in accordance with the manufacturer's instructions and agreement of the designer and supervisor as well.
|  | Podrum | Basement | m1 |  | 10 | 0
|  | Prizemlje | Ground floor | m1 |  | 24.7 | 0
|  | I sprat | First floor | m1 |  | 26.6 | 0
|  | Sala | Sports Hall | m1 |  | 1.5 | 0
XI. |  | PODOPOLAGAČKI RADOVI | FLOORING WORKS |  |  | Ukupno | 0
XII. |  | MOLERSKO-FARBARSKI RADOVI | PAINTING WORKS
82. |  | Bojenje i gletovanje zidova u školi: Obračun po m² sa pokretnom molerskom skelom | Painting and plastering the walls in the school: Calculation per m² with mobile scaffolding
|  | Podrum | Basement | m2 |  | 1581.45 | 0
|  | Prizemlje | Ground floor | m2 |  | 2733.68 | 0
|  | I sprat | First Floor | m2 |  | 2727.84 | 0
|  | Krovna lanterna | Roof latern | m2 |  | 241.52 | 0
83. |  | Bojenje i gletovanje plafona u školi: Obračun po m² kompletno sa pokretnom molerskom skelom. | Painting and plastering the walls in the school: Calculation per m² with mobile scaffolding
|  | Podrum | Basement | m2 |  | 1148.76 | 0
|  | Prizemlje | Ground floor | m2 |  | 1743.19 | 0
|  | I sprat | First Floor | m2 |  | 1547.21 | 0
|  | Krovna lanterna | Roof latern | m2 |  | 457.24 | 0
84. |  | Sanacija, bojenje i gletovanje zidova u sali: Obračun po m² kompletno sa pokretnom molerskom skelom. | Reparation, painting and plastering of the walls in the hall: Calculation per m² complete with mobile scaffolding. | m2 |  | 503 | 0
XII. |  | MOLERSKO-FARBARSKI RADOVI | PAINTING WORKS |  |  | Ukupno | 0
XIII. |  | FASADERSKI RADOVI | FAÇADE WORKS
85. |  | Izrada demit fasade fiskulturne sale sa termoizolacijom od mineralne vune debljine d=8cm, URSA GLASSWOOL FDP 1 i svim završnim slojevima navedenim u opštem opisu za izradu demit fasade. Fasadu završno bojiti u svemu prema grafičkim prilozima fasade i tehničkim opisima. Oznaka u projektu EW2.1 Fiskulturna sala_RAL 7036 | Construction of the demit facade of the Sport Hall with thermal insulation from mineral wool, thickness d=8cm, URSA GLASSWOOL FDP 1 and all finishing layers specified in the general description for the construction of the demit facade. Finish painting the facade in everything according to the graphic attachments of the facade and technical descriptions. Index in the EW2.1 project Gym_RAL 7036 | m2 |  | 806.41 | 0
86. |  | Izrada ventilisane fasadne obloga od aluminijumskih kompozitnih panela. Nabavka materijala, transport, izrada i ugradnja integrisanog fasadnog vješanog ventilisanog fasadnog sistema Alucobond ili ekvivalentno. ALUCOBOND A2 - kompozitna ploča sastavljena od 2 aluminijumske ploče legure EN AW-5005A (AlMg1) 0,5 mm debljine između kojih se nalazi polimerno jezgro ispunjeno mineralima. Specifična težina ploče iznosi 7,6 kg/m2 za debljinu ploče od 4 mm. Alucobond PLUS ploče ispunjavaju klasu negorivosti DIN EN 13501-1 klasa A2-s1, d0 Cijena obuhvata sav materijal, rad i potrebnu skelu. U cijenu fasade ulazi i ugradnja termoizolacije od mineralne vune URSA FDP 1 ili ekvivalentno, debljin d=8cm ispod ploče prizemlja, i ugradnja paropropusne vodoneporpusne folije preko termoizolacije a ispod aluminijskih kompozitnih panela. Oznake u projektu: C3.1; EW4.0; EW4.1; EW4.2; EW4.3; EW4.4; EW4.5 | Procurement of materials, transport, production and installation of an integrated facade suspended ventilated facade system Alucobond or equivalent. ALUCOBOND A2 - a composite plate composed of 2 aluminum plates of EN AW-5005A alloy (AlMg1) 0.5 mm thick, between which there is a polymer core filled with minerals. The specific weight of the board is 7.6 kg/m2 for a board thickness of 4 mm. Alucobond PLUS boards fulfill the non-flammability class DIN EN 13501-1 class A2-s1, d0. The price includes all materials, , labour and scaffolding. The price of facade includes installation of the thermal insulation made of mineral wool URSA FDP 1 or equivalent, tickness d=8cm under the ground floor slab, installation of a vapor-permeable waterproof foil over the thermal insulation and under the aluminum composite panels. Project indexes: C3.1; EW4.0; EW4.1; EW4.2; EW4.3; EW4.4; EW4.5
|  | Fasadni zidovi, Boja(Platinum Grey no. 136) ili ekvivalentno | Facade walls COLOUR (Platinum Grey no. 136) or equivalent | m2 |  | 1990.82 | 0
|  | Fasadni zidovi lanterna, Boja(Platinum Grey no. 136) ili ekvivalentno | Facade walls latern COLOUR (Platinum Grey no. 136) or equivalent | m2 |  | 260.42 | 0
|  | Vertikalni zidovi trijema, Boja( Coco Bolo no. 834) ili ekvivalentno | Vertical walls of the porch COLOUR ( Coco Bolo no. 834) or equivalent | m2 |  | 137.3 | 0
|  | Plafon trijema, Boja( Coco Bolo no. 834) ili ekvivalentno | Ceiling of the porch COLOUR ( Coco Bolo no. 834) or equivalent | m2 |  | 139.3 | 0
87. |  | Nabavka i ugradnja vertikalne termoizolacije u dijelu ventilisane fasade škole i trijemovima, d=10, 8, 5, 3cm. Tip: URSA FDP 1 ili ekvivalentno | Procurement and installation of vertical thermo insullation of the part of the school's ventilated facade and porches, d=10, 8, 5, 3cm.
|  | d=10cm | d=10cm | m2 |  | 26.08 | 0
|  | d=8cm | d=8cm | m2 |  | 1241.33 | 0
|  | d=5cm | d=5cm | m2 |  | 1004.21 | 0
|  | d=3cm | d=3cm | m2 |  | 26.67 | 0
XIII. |  | FASADERSKI RADOVI | FAÇADE WORKS |  |  | Ukupno | 0
XIV. |  | LIFT | ELEVATOR
88. |  | Nabavka i ugradnja električnog putničkog lifta nosivosti 630kg / 8 osoba, bez mašinske kućice u okviru liftovskog okna dimenzija 200x180cm. Dimenzije kabine 110x140cm. Vrata kabine i prilazna vrata dvokrilna širine 120cm visine 240cm, automatska teleskopska. Omogućen pristup licima sa invaliditetom. Dubina jame je 150cm. Broj stanica je 3. Visina od poda prve do poda poslednje stanice je 8.00m. Opremanje lifta po zelji Investitora. | Procurement and installation of an electric passenger elevator with a load capacity of 630 kg / 8 persons, without a machine room within the elevator shaft, dimensions 200x180 cm. Cabin dimensions 110x140cm. Cabin door and access door, double-leaf, width 120 cm, height 240 cm, automatic telescopic. Enabled access for persons with disabilities. The depth of the pit is 150 cm. The number of stations is 3. The height from the floor of the first to the floor of the last station is 8.00m. Equipping the elevator is up to the Investor. | kom/ pcs |  | 1 | 0
XIV. |  | LIFT | ELEVATOR |  |  | Ukupno | 0
XV. |  | RAZNI RADOVI | MISCELLANEOUS WORKS
89. |  | Izrada horizontalnih i vertikalnih dilatacionih spojnica. | Performing of horizontal and vertical expansion joints.
|  | Horizontalne dilatacione spojnice u podu | Horizontal expansion joints in floors | m1 |  | 19.48 | 0
|  | Horizontalne dilatacione spojnice u tavanici | Horizontal expansion joints in the ceiling | m1 |  | 19.48 | 0
|  | Vertikalne dilatacione spojnice u zidu | Vertical expansion joints in the wall | m1 |  | 16.92 | 0
|  | Izrada krovne dilatacione spojnice | Performing of the roof dilatation joints | m1 |  | 30.6 | 0
90. |  | Nabavka, i ugradnja taktilnih traka za upozorenje osobama sa invaliditetom i reljefnog orijentacionog plana. Trake sadrže ispupčenja koja upozoravaju ili usmjeravaju slijepe i slabovide osobe o postojanju prepreke ili oblasti u kojoj je kretanje otežano, kao što su na primer stepenice. Taktilne trake se postavljaju u skladu sa Pravilnikom o bližim uslovima i načinu prilagođavanja objekata za pristup i kretanje lica smanjenje pokretljivosti i lica sa invaliditetom. Pristupačna taktilna površina izvodi se reljefnom obradom visine do 5 mm na način da ne otežava kretanje invalidskih kolica, da je prepoznatljiva na dodir stopala ili bijelog štapa, da ne zadržava vodu, snijeg i nečistoću, i da se lako održava. Dostupne su u 3 formata: gumene ploče koje se lijepe, poliuertanske samoljepljive trake u kvadratnom i pravougaonom formatu. | Procurement and installation of tactile warning strips for people with disabilities and a relief orientation plan. The tactile paving strips consist protrusions that alert blind and visually impaired individualls to an abstacles or hazard that stands on their way or an area where movement is difficula, such as stairs. Tactile tapes are placed in accordance with the Rulebook on more conditions and methods of adapting facilities for access and movement of persons with reduced mobility and persons with disabilities. The accessible tactile surface is made with a relief treatment up to 5 mm height in such a way that it does not interfere with the movement of the wheelchair, tand to be recognized by the touch of the foot or a white stick, not retain water. , snow and dirt and to be easy maintaned. 3 formats are available: self-adhesive rubber strips, polyurethane self-adhesive strips in square and rectangular formats. | pauš./ LS |  | 1 | 0
91. |  | Mreža za zaštitu zidova i prozora od lopte u fiskulturnoj sali: Nabavka, isporuka i instalacija slobodnovisećih zaštitnih mreža. Mreža bijela, okca 10cm x 10cm. U kompletu ankeri, sajle, nosači, zatezači i sav potreban materijal za montažu. | Nets that protect windows and walls from bumping ball in the sports hall: Procurement, delivery and installation of free-hanging protecting nets. White net, size of 10 cm x 10cm. The set includes anchors, cables, supports, tensioners and all necessary material for assembly.
|  | Mreža 16x6m, iza koševa | Net 16x6m, behind the baskets | kom/ pcs |  | 2 | 0
|  | Mreža 28x3m, ispred prozora | Net 28x3m, in front of the windows | kom/ pcs |  | 2 | 0
92. |  | Završno čišćenje svih prostorija u objektu, pranje prozora, podova, zidova obloženih keramičkim pločicama i drugo. Čišćenje će se platiti samo jednom, bez obzira na broj izvršenih čišćenja u toku pripreme objekta za predaju. | Final cleaning of all rooms in the building, washing windows, floors, walls lined with ceramic tiles and more. Cleaning will be paid for only once, regardless of the number of cleanings performed during the preparation of the facility for handover. | m2 |  | 5641.3 | 0
93. |  | Nabavka, izrada i montaža table sa nazivom škole na zidu u trijemu. Tabla dimenzija 40x30cm izrađena od crnog pleksiglasa/klirita, sa skrivenim kačenjem na zid. | Procurement, production and installation of school name sign board on the wall in the porch. Board dimensions of 40x30cm made is black plexiglass/clearite, with hidden hanging on the wall. | kom/ pcs |  | 1 | 0
94. |  | Nabavka, izrada i montaža table sa nazivom projektanta i izvođača radova sa godinom izgradnje na zidu u trijemu. Tabla dimenzija 40x30cm izrađena od crnog pleksiglasa/klirita, sa skrivenim kačenjem na zid. | Procurement, production and installation of a board with the name of the designer and contractor along with the year of construction on the wall in the porch. Board of 40x30 cm size made of black plexiglass/clearite, with hidden hanging on the wall. | kom/ pcs |  | 1 | 0
95. |  | Nabavka, izrada i montaža lajsni kod kamenih oblutaka. Lajsne se postavljaju između kamenih oblutaka i zemlje i služe kao zaštita od rasipanja oblutaka. Obračun po m dužnom lajsne. | Procurement, production and installation of moldings for stone pebbles. Moldings are placed between stone pebbles and the ground and serve as protection against the scattering of pebbles. Calculation per square meter of moldings. | m1 |  | 171.78 | 0
96. |  | Nabavka, izrada i montaža zasjenjivača unutar škole. Zasjenjivači se postavljaju u enterijeru, uz strukturalnu fasadu i prate njenu širinu. Visina rolo sjenila u suterenu 315cm, na prizemlju 240cm i na spratu 320cm. Obračun po m dužnom rolo sjenila. | Procurement, production and installation of shaders inside the school. Shades are installed in the interior, next to the structural facade and follow its width. The height of the roller shades in the basement is 315 cm, on the ground floor 240 cm and on the first floor 320 cm. Calculation per square meter of blinds.
|  | Obračun po komadu, širina 225 (prizemlje) | Calculation per piece225, width (ground floor) | kom/ pcs |  | 4 | 0
|  | Obračun po komadu, širina 220 (prizemlje) | Calculation per piece, 220 width (ground floor) | kom/ pcs |  | 48 | 0
|  | Obračun po komadu, širina 195 (prizemlje) | Calculation per piece, 195 width(dround floor) | kom/ pcs |  | 2 | 0
|  | Obračun po komadu, širina 225 (sprat) | Calculation per piece, 225 width(first floor) | kom/ pcs |  | 4 | 0
|  | Obračun po komadu, širina 220 (sprat) | Calculation per piece, 220 width (first floor) | kom/ pcs |  | 54 | 0
|  | Obračun po komadu, širina 195 (sprat) | Calculation per piece, 195 width (first floor) | kom/ pcs |  | 2 | 0
|  | Obračun po komadu, širina 100 (suteren) | Calculation per piece, 100 width (basement) | kom/ pcs |  | 4 | 0
|  | Obračun po komadu, širina 220 (suteren) | Calculation per piece, 220 width (basement) | kom/ pcs |  | 8 | 0
XV. |  | RAZNI RADOVI | MISCELLANEOUS WORKS |  |  | Ukupno | 0
1.1. |  | REKAPITLUACIJA - ARHITEKTONSKO GRAĐEVINSKI RADOVI | SUMMARY ARCHITECTURAL CONSTRUCTION WORKS
I. |  | PRIPREMNI RADOVI | PREPARATION WORKS |  |  |  | 0
II. |  | ZEMLJANI RADOVI | EARTHWORKS |  |  |  | 0
III. |  | BETONSKI I ARMIRANO-BETONSKI RADOVI | CONCRETE AND REINFORCED CONCRETE WORKS |  |  |  | 0
IV. |  | ARMIRAČKI RADOVI | REINFORCEMENT WORKS |  |  |  | 0
V. |  | ZIDARSKI RADOVI | MASONRY WORKS |  |  |  | 0
VI. |  | KROVOPOKRIVAČKI I LIMARSKI RADOVI | ROOFING AND SHEET METAL WORKS |  |  |  | 0
VII. |  | IZOLATERSKI RADOVI | INSULATION WORKS |  |  |  | 0
VIII. |  | GIPSARSKI RADOVI | PLASTERING WORKS |  |  |  | 0
IX. |  | STOLARSKI I BRAVARSKI RADOVI | JOINERY AND LOCKSMITHING WORKS |  |  |  | 0
X. |  | KERAMIČARSKI RADOVI | CERAMIC WORKS |  |  |  | 0
XI. |  | PODOPOLAGAČKI RADOVI | FLOORING WORKS |  |  |  | 0
XII. |  | MOLERSKO-FARBARSKI RADOVI | PAINTING WORKS |  |  |  | 0
XIII. |  | FASADERSKI RADOVI | FAÇADE WORKS |  |  |  | 0
XIV. |  | LIFT | ELEVATOR |  |  |  | 0
XV. |  | RAZNI RADOVI | MISCELLANEOUS WORKS |  |  |  | 0
1.1. |  | REKAPITULACIJA - ARHITEKTONSKO GRAĐEVINSKI RADOVI | SUMMARY ARCHITECTURAL CONSTRUCTION WORKS |  |  |  | 0

## 1.2. Uređenje terena - LANDSCAP
Program obrazovanja Crne Gore/ Education program of Montenegro
Predmjer - Izgradnja nove OŠ "Vladimir Nazor"/ Bill of Quantity - Construction of the new Elementary School "Vladimir Nazor" UREĐENJE TERENA /LANDSCAPING - ARCHITECTURE
br/ No | predmet / subject | NASLOV | DESCRIPTION | mj.jedinica/ unit | pred.cijena u eurima/ unit price € | Količina / Quantity | Cijena u eurima (bez PDV-a) / Amount in € (excl VAT)
(a) | (b) | (c) |  | ( d ) | (e) | (f) | (g=e*f)
1.2. |  | UREĐENJE TERENA | LANDSCAPING - ARCHITECTURE
|  | PREDMJER I PREDRAČUN UREĐENJA TERENA | BILL OF QUANTITY OF LANSCAPING
I. |  | PRIPREMNI RADOVI | PREPARATORY WORKS
1. |  | Rušenje postojeća dva nenatkrivena betonska sportska terena sa postojećim mobilijarom mehanizacijom i ručno gdje je neophodno. Uklonjeni šut utovariti i odvesti na deponiju. U cijenu ulazi sva neophodna mehanizacija, rad i transport šuta na deponiju. | Demolition of the existing two uncovered concrete sports fields with the existing furniture by the mechanical way and by hand where necessary. Load the removed rubble and transport it to the landfill. The price includes all the required mechanization, work and transport of debris to the landfill. | m2 |  | 1296.12 | 0
2. |  | Rušenje postojećeg objekta na istočnom dijelu parcele, mehanizacijom i ručno gdje je neophodno. Uklonjeni šut utovariti i odvesti na deponiju. U cijenu ulazi sva neophodna mehanizacija, rad i transport šuta i metala na deponiju. | Demolition of the existing facility on the eastern part of the parcel, with machinery and by hand, where necessary. Load the removed debris and transport it to the landfill. The price includes all the required machinery, work and transport of waste and metal to the landfill. | m2 |  | 14.5 | 0
3. |  | Uklanjanje postojeće betonske staze kojoj se pristupa sa istoka, iz ulice Vuka Mićunovića. Uklonjeni šut utovariti i odvesti na deponiju. U cijenu ulazi sva neophodna mehanizacija, rad i transport šuta i metala na deponiju. | Removal of the existing concrete path accessed from the east, from Vuk Micunovic Street. Load the removed debris and transport it to the landfill. The price includes all necessary mechanization, work and transport of waste and metal to the landfill. | m2 |  | 21.35 | 0
I. |  | PRIPREMNI RADOVI | PREPARATORY WORKS |  |  | Ukupno/ total | 0
II. |  | ZEMLJANI RADOVI | EARTHWORKS
|  | ISKOP | EXCAVATION
4. |  | Iskop zemlje za temeljni zid betonskih klupa u zoni pristupnog trga mašinskim putem, u tlu II do III kategorije. Iskop izvesti do potrebne dubine od 40cm, prema detalju klupe i datim kotama. Iskopani materijal deponovati u okviru gradilišta za kasnija nasipanja. Cijena obuhvata otkop i deponovanje na gradilišnu deponiju. | Excavation of soil for the foundation wall of concrete benches in the area of the access square by machine in the ground of categories II to III. Excavate to the required depth of 40 cm, according to the detail of the bench and given elevations. Deposit the excavated material within the construction site for later embankments. The price includes excavation and depositing at the construction site landfill. | m3 |  | 2 | 0
5. |  | Iskop zemlje za temeljni zid ograde mašinskim putem, u tlu II do III kategorije. Iskop izvesti do potrebne dubine za temeljni zid (prosječno 80cm), prema šemama i datim kotama. Iskopani materijal deponovati u okviru gradilišta za kasnija nasipanja. Cijena obuhvata otkop i deponovanje na gradilišnu deponiju. | Excavation of soil for the foundation wall of the fence by machine in the ground of categories II to III. Excavate to the required depth for the foundation wall (average 80 cm), according to the graphical documentation and given elevations. Depose the excavated material within the construction site for later embankments. The price includes excavation and deposing at the construction site landfill. | m3 |  | 265.5 | 0
6. |  | Iskop zemlje ispod popločanih staza koje vode od trga do parking prostora i atletske staze, u tlu II do III kategorije. Iskop izvesti do potrebne dubine (prosječno 20-25cm) iznad koje se vrši tamponiranje sa svim neophodnim slojevima, u svemu prema visinskim kotama na situacijama. Iskopani materijal deponovati u okviru gradilišta za kasnija nasipanja. Cijena obuhvata otkop i deponovanje na gradilišnu deponiju. | Excavation of soil under the paved pathways from the square to the parking area and the athletic track in the ground of categories II to III. Excavate to the required depth (on average 20-25cm), above which filling of crushed stone material is carried out in the necessary layers, according to the elevations of the Landscape Design. Depose the excavated material within the construction site for later embankments. The price includes excavation and deposing at the construction site landfill. | m3 |  | 50 | 0
7. |  | Iskop zemlje ispod pristupnog trga u tlu II do III kategorije. Iskop izvesti do potrebne dubine iznad koje se vrši tamponiranje sa svim neophodnim slojevima, u svemu prema visinskim kotama na situacijama. Iskopani materijal deponovati u okviru gradilišta za kasnija nasipanja. Cijena obuhvata otkop i deponovanje na gradilišnu deponiju. | Excavation of the ground under the access square in the soil of categories II to III. Excavate to the required depth above which filling of crushed stone material is carried out in the necessary layers, according to the elevations of the Landscape Design. Depose the excavated material within the construction site for later embankments. The price includes excavation and deposing at the construction site landfill. | m3 |  | 10 | 0
|  | NASIPANJE ZEMLJE | BACKFILLING
8. |  | Nasipanje i nabijanje usitnjene zemlje ispod trga u skladu sa projektom uređenja terena. Zemlju nasipati u slojevima u prosjeku od 10 do 20cm, kvasiti vodom, nabijati vibro valjkom do potrebne zbijenosti, uvaljati i nivelisati po projektu. Za nasipanje koristiti zemlju deponovanu prilikom iskopa. Cijena obuhvata nasipanje i nabijanje zemlje iz iskopa do potrebne zbijenosti. | Backfilling and compaction of shredded soil under the square by the Landscaping Design. Fill the soil in layers of 10 to 20 cm on average, moisten it with water, and compact it with the vibration roller to the required compaction, rolling and levelling according to the Design. For filling, use the earth deposited during excavation. The price includes filling and compaction of the soil from the excavation to the required compaction. | m3 |  | 45 | 0
9. |  | Nasipanje i nabijanje usitnjene zemlje ispod površina atletske staze. Zemlju nasipati u slojevima od 20cm u skladu sa projektom uređenja terena, kvasiti vodom, nabijati vibro valjkom do potrebne zbijenosti, uvaljati i nivelisati po projektu. Za nasipanje koristiti zemlju deponovanu prilikom iskopa. Cijena obuhvata nasipanje i nabijanje zemlje iz iskopa do potrebne zbijenosti. | Backfilling and compaction of shredded soil under the surfaces of the athletics track. Fill the soil in layers of 20 cm by the Landscaping Design, moisten it with water, and compact it with a vibratory roller to the required compaction, rolling and levelling according to the Design. For filling, use the earth deposited during excavation. The price includes filling and compaction of the soil from the excavation to the required compaction. | m3 |  | 22 | 0
10. |  | Nasipanje i nabijanje usitnjene zemlje oko objekta škole, pristupnog trga i staza u neposrednoj zoni škole do kote terena u skladu sa projektom uređenja terena, sa svim neophodnim padovima koji omogućavaju odvodnju atmosferskih voda sa terena. Zemlju nasipati u slojevima od 20cm, kvasiti vodom, nabijati vibro valjkom do potrebne zbijenosti, uvaljati i nivelisati po projektu. Za nasipanje koristiti zemlju deponovanu prilikom iskopa. Cijena obuhvata nasipanje i nabijanje zemlje iz iskopa do potrebne zbijenosti. | Filling and compaction of shredded earth around the school building, the access square and paths in the immediate area of the school up to the ground level by the Landscaping Design, with all the necessary falls that allow the drainage of stormwater from the ground. Fill the soil in layers of 20 cm, moisten it with water, and compact it with the vibratory roller to the required compaction, roll and level according to the Design. For filling, use the earth deposited during excavation. The price includes filling and compaction of the soil from the excavation to the required compaction | m3 |  | 458 | 0
|  | RAZASTIRANJE ŠLJUNKA | GRAVEL SPREADING
11. |  | Nabavka, prevoz i razastiranje tamponskog sloja šljunka granulacije 16-32mm, u sloju debljine 10cm, ispod temelja ograde i temelja betonskih klupa. Tamponski sloj šljunka nasuti u slojevima, nabiti i nivelisati po projektu i šemama, sa tolerancijom po visini +/- 1cm. | Procurement, transport and spreading of the layer of 16-32mm coarse gravel, in a 10cm thick layer, under the foundation of the fence and the foundation of the concrete benches. The layer of gravel is spread in layers, compacted and levelled according to the Design and drawings, with a height tolerance of +/- 1cm. | m3 |  | 28.8 | 0
12. |  | Nabavka, prevoz i razastiranje tamponskog sloja šljunka kao donjeg nosivog sloja granulacije 0-63mm, u sloju debljine 25cm, ispod površina koje se popločavaju betonskim pločama. Tamponski sloj šljunka nasuti u slojevima, nabiti i nivelisati po projektu i šemama, sa tolerancijom po visini +/- 1cm. | Procurement, transporttion and spreading of the layer of gravel as a lower load-bearing layer with granulation of 0-63 mm, in a layer 25 cm thick, under the surfaces, to be paved with concrete slabs. The layer of gravel is spread in layers, compacted and levelled according to the Design and drawings, with a height tolerance of +/- 1cm.
|  | Ispod pristupnog trga | the pathway from the square to the parking area and the athletics track | m3 |  | 112.28 | 0
|  | Staza od trga do parking prostora i atletske staze | the pathway from the square to the parking area and the athletics track | m3 |  | 120.62 | 0
13. |  | Nabavka, prevoz i razastiranje tamponskog sloja tucanika (drobljenog kamena) granulacije 0-31.5mm, u sloju debljine 25cm, ispod atletske staze i sportskog terena. Tamponski sloj šljunka nasuti u slojevima, nabiti i nivelisati po projektu i šemama, sa tolerancijom po visini +/- 1cm. | Procurement, transport and spreading of the layer of crushed stone (crushed stone) granulation 0-31.5 mm, in a layer 25 cm thick, under the athletic track and sports field. The tampon layer of crushed stone is spread in layers, compacted and levelled according to the design and drawings, with a height tolerance of +/- 1cm. | m3 |  | 160.64 | 0
II. |  | ZEMLJANI RADOVI | EARTHWORKS |  |  | Ukupno/ total | 0
III. |  | BETONSKI I ARMIRANO-BETONSKI RADOVI | CONCRETE AND REINFORCED CONCRETE WORKS
14. |  | Armirano betonski temelji Izrada armirano-betonskog temeljnog zida ograde, širine 50cm u dnu i 20cm na vrhu, i visine 70cm prema detalju u projektu uređenja terena, od betona marke MB30 u potrebnoj ivičnoj oplati. Temelje armirati po projektu, detaljima i statičkom proračunu. Beton ugraditi i njegovati po propisima. | Construction of the reinforced concrete foundation wall of the fence, 50 cm wide at the bottom and 20 cm at the top, and 70 cm high, according to the detail in the Landscaping Design, from concrete, class MB 30, in the necessary edge formwork. Reinforcement of the foundations according to the Design, details and static calculation. Install and maintain concrete according to regulations | m3 |  | 125.85 | 0 | 150
15. |  | Betonske ploče parternog uređenja Nabavka, prevoz i ugradnja dvoslojnih lux betonskih ploča prane površine proizvođača BOSSIN ili ekvivalentno. Ploče su dimenzija 60x30cm i debljine 5cm. Ugrađuje se nijansa Narona bijela koja pokriva polja pristupnog trga i staza do parking prostora i atletske staze. Postupak ugradnje betonskih elemenata zahtijeva određeni postupak koga se treba pridržavati. Određivanje visinskih kota, dovoljna debljina i sabijenost tampon sloja, preciznost u montaži ploča i pravilan izbor materijala su samo neki od uslova da bi se dobila kvalitetna, izdržljiva i estetski lijepa površina. Preporuka je da se betonski elementi polažu isključivo na sloju pijeska ili sitne kamene rizle. Na ovaj način se prije svega dobija mogućnost lake zamjene oštećenih ploča, lake demontaže pri eventualnim intervencijama na podzemnim instalacijama, kao i bržeg odvođenja površinske vode u drenažni sloj. U cijenu pozicije ulazi i razastiranje sloja rizle 4cm u koji se polažu ploče. | Procurement, transport and installation of two-layer lux concrete slabs with the washable surface manufactured by BOSSIN or equivalent. The slabs have dimensions of 60x30cm and are 5cm thick. The shade of the slabs is Narona white for covering the fields of the access square and the pathways to the parking area and the athletics track. The process of installing concrete elements requires a specific procedure that must be followed. Determining the heights, sufficient thickness and compaction of the crushed stone layer, precision in the installation of slabs and the correct choice of materials are just some conditions to obtain the high-quality, durable and aesthetically pleasing surface. Furthermore, it is recommended that concrete elements be paved exclusively on the layer of sand or small stone particles. In this way, the replacement of damaged plates and disassembly during possible interventions on underground installations are accessible, as well as faster surface water drainage into the drainage layer. The price of the position includes spreading the 4 cm layer of sand in which the slabs are installed.
|  | pristupni trg NARONA BIJELA | Access square NARONA WHITE | m2 |  | 449.12 | 0
|  | staza od trga do parking prostora i atletske staze NARONA BIJELA | The path from the square to the parking area and the athletics track NARONA WHITE | m2 |  | 482.48 | 0
16. |  | Betonske klupe Izrada armirano-betonskih prefabrikovanih klupa, presjeka prema detalju u projektu, od betona marke MB 30, otpornosti na mraz MM100. Klupa je dužine 480cm, širine 60cm i visine 45cm. Klupa sadrži u sebi rupu prečnika 40cm i dubine 30cm, namijenjenu za ugradnju limenih kanti za otpatke. Klupu izraditi u glatkoj oplati sa podupiračima a nosače armirati po projektu, detaljima i statičkom proračunu. Betoniranje vršiti odgovarajućim agregatom kako bi se dobila što veća glatkoća površine. Koristiti sivu boju agregata, kako bi se dobila hladna bijela boja. Beton ugraditi i njegovati po propisima. U cijenu ulaze i oplata, podupirači i pomoćna skela. Broj komada je 6. | Concrete benches: Production of reinforced concrete prefabricated benches, cross-section according to the detail in the Design, from concrete class MB 30, frost resistance MM100. The bench is 480 cm long, 60 cm wide and 45 cm high. The bench contains a hole with a diameter of 40 cm and a depth of 30 cm, intended to install metal garbage cans. Make the bench in smooth formwork with supports and reinforcement the supports according to the Design, details and static calculation. Concreting should be done with the appropriate aggregate to obtain the surface's most excellent smoothness. Use the grey colour of the aggregate to get a cool white colour. Install and maintain concrete according to regulations. The price includes formwork, supports and additional scaffolding. The number of pieces is 6. | m3 |  | 7.77 | 0
17. |  | Armirano-betonski temelj za jarbole Izrada armirano-betonskog temelja-stope za jarbole dimenzija 30x30cm (jedna polovina betonskih ploča na kraju) i dubine 80cm, od betona marke MB30 u potrebnoj ivičnoj oplati. Temelj armirati po projektu, detaljima i statičkom proračunu. Beton ugraditi i njegovati po propisima. | Production of reinforced concrete foundation feet for masts with dimensions of 30x30cm (one-half of the concrete slabs at the end) and the depth of 80cm from concrete class MB30 in the necessary edge formwork. Reinforcement of the foundation according to the Design, details and static calculation. Install and maintain concrete according to regulations. | m3 |  | 0.5 | 0
18. |  | Betonska česma Izrada betonske česme dimenzija 60x30cm i visine 120cm u svemu prema projektu. Korito česme se u punoj visini ukopava u zemlju. Česma se polaže na sloju dobro nabijenog šljunka. Česmu izraditi u glatkoj oplati sa podupiračima a nosače armirati po projektu, detaljima i statičkom proračunu. Betoniranje vršiti odgovarajućim agregatom kako bi se dobila što veća glatkoća površine. Koristiti sivu boju agregata, kako bi se dobila hladna bijela boja. Beton ugraditi i njegovati po propisima. U cijenu ulaze i oplata, podupirači i pomoćna skela. | Concrete Outdoor Drinking Fountain: Making of the outdoor concrete drinking fountain with dimensions of 60x30cm and the height of 120cm according to the Design. The trough of the fountain is placed into the ground at full height. The fountain is installed on the layer of well-compacted gravel. The fountain is made in smooth formwork with supports, and the supports are reinforced according to the Design details and static calculation. Concreting should be done with the appropriate aggregate to obtain the most excellent test smoothness of the surface. Use the grey colour of the aggregate to get a cool white colour. Install and maintain concrete according to regulations. The price includes formwork, supports and auxiliary scaffolding | kom/pcs |  | 2 | 0
III. |  | BETONSKI I ARMIRANO-BETONSKI RADOVI | CONCRETE AND REINFORCED CONCRETE WORKS |  |  | Ukupno/ total | 0
IV. |  | ARMIRAČKI RADOVI | REINFORCEMENT WORKS
19. |  | Količina armature data je za temelj ograde i betonske klupe a za obračun sa Investitorom služiće planovi i specifikacije armature, kao i građevinska knjiga. | The quantity of reinforcement is given for the foundation of the fence and the concrete bench, and the plans and specifications of the reinforcement, as well as the construction book, will be used for the settlement with the Investor.
|  | Temelj ograde | The foundation of the fence | kg |  | 6607.8 | 0
|  | Betonske klupe (6 komada) | Concrete benches (6 pieces) | kg |  | 511.8 | 0
IV. |  | ARMIRAČKI RADOVI | REINFORCEMENT WORKS |  |  | Ukupno/ total | 0
V. |  | BRAVARSKI RADOVI | METAL-FENSING WORKS
20. |  | Kapija za vozila Dvije dvokrilne ulazne kapije (oznaka G02 i G03 u projektu) za vozila širine 2x300cm osno i 2x285cm osno, visine 120cm sa otvaranjem krila klizno u stranu putem točkića i podne šine. Krilo se pakuje u dupli P profil na spoju dva krila i u po jedan P profil na krajevima krila. Konstrukcija krila je od vertikalnih čeličnih kutija 40x20 (debljine zida 2mm) visine 118cm, i horizontalnih čeličnih kutija rukohvata i donje šipke dimenzija 40x20cm, dužine u svemu prema detalju u projektu. Ispune su od čeličnih šipki 20x20 (debljine zida 1,5mm) visine 114cm na osnom rastojanju od 15cm. Okov za otvaranje i fiksiranje kapije - kvalitetan. Kapija je opremljena odgovarajućom bravom sa tri ključa i kvakom sa obje strane. Kapija za vozila se otvara na elektromehanički pogon, tipa Mastnak sistema ili ekvivalentno, te sadrži elektronsku kontrolnu jedinicu i prijemnik za radio-frekvencijsko upravljanje. U vanrednim okolnostima, dati mogućnost za deblokiranje motora i ručno otvaranje kapije. Ugraditi podni graničnik. Svi metalni djelovi su od galvanizovanog čelika. Ogradu premazati antikorozivnim premazem i sa minimum dva sloja metalizirane silikonske antracit boje visokog stepena otpornosti na hemijske i mehaničke uticaje. | Vehicle gate Two double-leaf entrance gates (marking G02 and G03 in the Design) for vehicles with dimensions: a width of 2x300cm and 2x285cm on the axis, a height of 120cm with the sliding opening of the leaves to the side using wheels and the floor rail. The limiters for the sliding leaves are made of a U profile at both ends of the gate. The construction of the leaves is made of vertical steel boxes 40x20 (wall thickness 2mm) 118cm high, horizontal steel boxes for the handle and the lower bar measuring 40x20cm, the length in all according to the detail in the Design. The fillings are made of steel bars 20x20 (wall thickness 1.5mm) 114cm high at an axial distance of 15cm. Hardware for opening and fixing the gate must be high quality. The gate has an appropriate lock with three keys and a handle on both sides. The vehicle gate opens with an electromechanical drive of the Mastnak system type or equivalent and contains an electronic control unit and a receiver for radio-frequency control. In emergencies, provide the possibility to unlock the motor and open the gate manually. Install the floor stop. All metal parts are made of galvanized steel. Coat the fence with an anti-corrosive coating and at least two layers of metallized silicone anthracite paint with a high degree of resistance to chemical and mechanical influences.
|  | G02: 2x300x120cm | G02: 2x300x120cm | kom/ pcs |  | 1 | 0
|  | G03: 2x285x120cm | G03: 2x285x120cm | kom/ pcs |  | 1 | 0
21. |  | Ulazna kapija na trgu Jednokrilna ulazna kapija (oznake G01 u projektu) širine 405cm i visine 120cm osno sa otvaranjem krila klizno u stranu putem točkića i podne šine. Krilo se pakuje u P profil na oba svoja kraja. Konstrukcija krila je od vertikalnih čeličnih kutija 40x20 (debljine zida 2mm) visine 118cm na osnom rastojanju od 405cm i horizontalnih čeličnih kutija rukohvata i donje šipke dimenzija 40x20mm dužine 407cm. Ispune su od čeličnih šipki 20x20mm (debljine zida 1,5mm) visine 114cm na osnom rastojanju od 15cm. Kapija se otvara ručno. Okov za otvaranje i fiksiranje kapije - kvalitetan. Kapija je opremljena odgovarajućom bravom sa tri ključa i kvakom sa obje strane. Svi metalni djelovi su od galvanizovanog čelika. Ogradu premazati antikorozivnim premazem i sa minimum dva sloja metalizirane silikonske antracit boje visokog stepena otpornosti na hemijske i mehaničke uticaje. Oznaka u projektu: G01: 405x120 cm | Entrance gate on the square Single-leaf entrance gate (labels G01 in the Design), dimension along the axis: a width of 405 cm and a height of 120 cm. The gate opens slidingly, using wheels and a sliding rail. The limiters for the sliding leaves are made of a U profile at both ends of the gate. The construction of the wings is made of vertical steel boxes 40x20mm (wall thickness 2mm) 118cm high at an axial distance of 405cm and horizontal steel boxes for handles and lower bars, dimension 40x20mm and 407cm long. The fillings are made of steel bars 20x20mm (wall thickness 1.5mm) 114cm high at an axial distance of 15cm. The gate is opened manually. Hardware for opening and fixing the gate must be of high quality. The gate has the appropriate lock with three keys and a handle on both sides. All metal parts are made of galvanized steel. Coat the fence with an anti-corrosive coating and at least two layers of metallized silicone anthracite paint with a high degree of resistance to chemical and mechanical influences. Marking in the Design: G01: 405x120 cm | kom/ pcs |  | 1 | 0
22. |  | Kapija za pješake Jednokrilna ulazna kapija širine 120cm i visine 120cm osno sa otvaranjem oko vertikalne ose. Konstrukcija krila je od vertikalnih čeličnih kutija 40x20mm (debljine zida 2mm) visine 118cm na osnom rastojanju od 120cm i horizontalnih čeličnih kutija rukohvata i donje šipke dimenzija 40x20mm. Ispune su od čeličnih šipki 20x20mm (debljine zida 1,5mm) visine 115cm na osnom rastojanju od 15cm. Kapija se otvara ručno. Okov za otvaranje i fiksiranje kapije - kvalitetan. Kapija je opremljena odgovarajućom bravom sa tri ključa i kvakom sa obje strane. Svi metalni djelovi su od galvanizovanog čelika. Ogradu premazati antikorozivnim premazem i sa minimum dva sloja metalizirane silikonske boje antracit visokog stepena otpornosti na hemijske i mehaničke uticaje. Oznaka u projektu: G04: 120x120 cm | Pedestrian gate A single-leaf entrance gate, dimension along the axis: a width of 120 cm and a height of 120 cm, the opening around the vertical axis. The construction of the leaves is made of vertical steel boxes 40x20mm (wall thickness 2mm) 118cm high at an axial distance of 120cm and horizontal steel boxes for the handles and the lower bar, dimension 40x20mm. The fillings are made of steel bars 20x20mm (wall thickness 1.5mm) 115cm high at the axial distance of 15cm. The gate is opened manually. Hardware for opening and fixing the gate must be high quality. The gate has an appropriate lock with three keys and a handle on both sides. All metal parts are made of galvanized steel. Coat the fence with an anti-corrosive coating and at least two layers of anthracite metallized silicone paint with high resistance to chemical and mechanical influences Marking in the Design: G04: 120x120 cm | kom/ pcs |  | 1 | 0
23. |  | Ograda Ograda se montira na armirano-betonski temelj. Radi se u poljima od po 150cm dužine i visine 120cm osno. Konstrukcija krila je od vertikalnih čeličnih kutija 40x20mm (debljine zida 2mm) visine 118cm ankerisanih ili ubetoniranih u armirano-betonski temelj na osnom rastojanju od 150cm. Polje-ispuna se sastoji od rukohvata dimenzija 40x20mm dužine 150cm i donje šipke dimenzija 40x20mm dužine 148cm. Ispune su od čeličnih šipki 20x20mm (debljine zida 1,5mm) visine 115cm na osnom rastojanju od 15cm. Polja-ispune se kače na konstrukciju - vertikalnu čeličnu kutiju sa prepustom od 1cm, dok se međusobni spojevi polja vare a potom bruse, poliraju i adekvatno tretiraju sredstvima za metal. Svi metalni djelovi su od galvanizovanog čelika. Ogradu premazati antikorozivnim premazem i sa minimum dva sloja metalizirane silikonske boje antracit visokog stepena otpornosti na hemijske i mehaničke uticaje. Oznaka u projektu:RL10 - segment 150cm dužine, h=120 cm | Fence: The fence is installed on the reinforced concrete foundation. It is done in fields of 150 cm in length and 120 cm in height. The leaf's construction is made of vertical steel boxes 40x20mm (wall thickness 2mm) 118cm high, anchored or concreted into the reinforced concrete foundation at an axial distance of 150cm. The fillings consist of the handle measuring 40x20mm, length 150cm and a lower bar measuring 40x20mm, length 148cm. The fillings are made of steel bars 20x20mm (wall thickness 1.5mm) 115cm high at an axial distance of 15cm. The fields-fillings are hung on the construction - the vertical steel box with an overhang of 1 cm, while the joint joints of the fields are welded and then ground, polished and adequately treated with coating for metal. All metal parts are made of galvanized steel. Coat the fence with an anti-corrosive coating and at least two layers of anthracite metallized silicon paint high degree of resistance to chemical and mechanical influences. Marking in the Design:RL10 - segment 150cm length, h=120 cm | m1 |  | 547 | 0
V. |  | BRAVARSKI RADOVI | METAL-FENSING WORKS TOTAL |  |  | Ukupno/ total | 0
VI. |  | SPORTSKA OPREMA | SPORTS EQUIPMENT
24. |  | Košarka Nabavka i ugradnja takmičarske jednocijevne košarkaške konstrukcije visine 225cm. Konstrukcija koša metalna, finalno obojena zaštićena od atmosferskih uticaja sa prednjom mekom zaštitom. Košarkaška tabla staklena (minimalne debljine 10mm u metalnom ramu sa mekom zaštitom. U kompletu profesionalni pregibni obruč sa ručno pletenom mrežom. Boja konstrukcije crna. Boja mekih zaštita stubova i staklene table crna. | Basketball Procurement and installation of the competitive single-tube basketball structure with a height of 225 cm. The basket's construction is metal, finally painted, protected from atmospheric influences with front soft protection. Glass basketball backboard (minimum thickness 10mm in the metal frame with soft protection. Complete with the professional folding hoop with a hand-knitted net. The construction colour is black. The colour of the posts' soft protection and the glass backboard is black. | kom/ pcs |  | 1 | 0
VI. |  | SPORTSKA OPREMA | SPORTS EQUIPMENT |  |  | Ukupno/ total | 0
VII. |  | RAZNI RADOVI | MISCELLANEOUS WORKS
25. |  | Izrada sportskih površina od tartana: Nabavka, transport i ugradnja STOBITAN SC dvoslojne, vodopropusne sportske podloge pogodne kako za treniranje tako i za takmičenja. Podloga je namijenjena svim sportovima na otvorenom prostoru. Podloga mora biti otporna na UV zračenja, atmosferske uticaje i da bude postojana. Osnovni sloj se sastoji iz recikliranih gumenih granulata (SBR) crne boje koje su povezane poliuretanom i postavljanje se vrši tzv. finišerima. Završni sloj se šprica u dva sloja sa specijalnim poliuretanskim vezivom i sitnim EPDM granulatom. Ukupna debljina podloge je 13mm. Boja podloge je tamno zelena. U cijenu uračunato obiljležavanje sportskih terena linijama širine 5cm po propozicijama takmičenja. Podloga mora da poseduje EN 14877 standard i IAAF sertifikat što se dokumentuje uz ponudu. | The lining of sports surfaces with tartan: Supply, transport, and install STOBITAN SC two-layer, waterproof sports surface suitable for training and competitions. The surface is intended for all outdoor sports. The lining must be resistant to UV radiation and atmospheric influences and be durable. The base layer consists of recycled rubber granules (SBR) of black colour, which are connected with polyurethane, and the finishers carry out the installation. The final layer is sprayed in two layers with a special polyurethane binder and fine EPDM granules. The total thickness of the substrate is 13mm. The colour of the lining is dark green. The price includesmarking sports fields with 5 cm wide lines according to the competition's proposals. The surface must have the EN 14877 standard and the IAAF certificate documented with the offer. | m2 |  | 642.57 | 0
26. |  | Izrada asfaltiranih površina: Izrada asfalta u dva sloja i to: bitumizirani sloj BNS22 6cm i završni sloj asfalta 4cm, koji je mješavina kamenog agregata i bitumena. Kameni agregat mora biti oštrih ivica – tucanik (drobljeni kamen). Asfalt se polaže na uvaljani sloj tucanika u visini od 25 cm, koji ulazi u cijenu pozicije. U cijenu pozicije ulazi i ugradnja betonskih ivičnjaka IB6 ili slično, visine 25cm i širine 7cm sa vrhom od bijelog betona. Dužina ivičnjaka 100cm, težina 35kg/kom, boja sivi i bijeli beton. Ivičnjaci se ugrađuju uz sportske površine od tartana, kao ivična zona zaštite asfaltnog sloja i same tartanske površine. Ivičnjaci se ugrađuju sa obje strane atletske staze, odnosno sportskog terena. Ivičnjake ugrađivati u svemu prema uputstvima proizvođača i prema karakterističnim detaljima iz projekta. | Perform of asphalt surfaces: Performing of asphalt in two layers: bituminous layer BNS22 6 cm and the final layer of asphalt concrete 4 cm, which is the mixture of stone aggregate and bitumen. The stone aggregate must have sharp edges - crushed stone. Asphalt is placed on a rolled layer of crushed stone at the height of 25 cm, which is included in the price of the position. The work's price includes installing concrete curbs IB6 or similar, height 25cm and width 7cm with the top face from white concrete. Curb length 100cm, weight 35kg/piece, grey and white concrete. Curbs are installed next to tartan sports surfaces as an edge zone to protect the asphalt and tartan surfaces. Curbs are installed on both sides of the athletic track, i.e. the sports field. Curbs should be installed in everything according to the manufacturer's instructions and according to the characteristic details of the Design. | m2 |  | 642.57 | 0
27. |  | Podaščavanje betonskih klupa sa sjeđenje: Nabavka, prevoz i ugradnja drvenih gredica profila 5x5cm dužine 358cm na čeličnoj potkonstrukciji od flahova ankerisanih u betonsku klupu. Na klupi montirati podužno 11 gredica sa međusobnim razmakom od 0.5cm kako bi se stvorila kompaktna površina za sjeđenje. Grede ankerisati u čeličnu potkonstrukciju, poprečno, najmanje na 3 mjesta. Grede završno tretirati bezbojnim lakovima i bojom za drvo kako bi se osigurala njihova otpornost na atmosferalije. U cijenu ulazi metalna potkonstrukcija, drvene grede, bojenje greda i njihova ugradnja. | Wood cladding of concrete benches for sitting: Procurement, transportation and installation of wooden beams with dimensions of 5x5 cm and the length of 358 cm on the steel substructure made of beams anchored in a concrete bench. On the bench, install 11 beams along the bench with a distance of 0.5 cm between them to create a compact sitting surface. Then, anchor the beams into the steel substructure transversely, at least in 3 places. Finally, finish the beams with colourless varnishes and wood paint to ensure their resistance to weathering. The price includes the metal substructure, wooden beams, painting of the beams and their installation. | kom/ pcs |  | 6 | 0
28. |  | Kante za smeće: Izrada kante za otpatke od plastificiranog lima, debljine d=0,5mm, u otvorima predviđenim u okviru klupe. Kanta je visine 30cm i prečnika 40cm, sa oborenom pokrovnom pločom koja omogućava nesmetano vađenje kante zarad pražnjenja. Boja kante siva, sirovog lima. | Waste cans Perform the waste bin from plasticized sheet, thickness d=0.5mm, in the openings provided on the bench. The bin is 30cm high and 40cm in diameter, with a folded-down cover plate that allows easy removal of the bin for emptying. The colour of the bins is grey, raw sheet metal. | kom/ pcs |  | 6 | 0
29. |  | Parking za bicikla: Izrada metalnih parking mjesta za bicikla u svemu prema detaljima iz projekta. Parking za bicikla je dimenzija 70x70cm. Izrađuje se od metalnih kutijastih profila 5x2cm i ankeriše u pod na 3 mjesta. Parking mjesta se završno tretiraju premazima za metal i boje u crnoj boji. Montiranje parking mjesta se vrši na rastojanju od 120cm. | Bicycle parking Perform metal parking places for bicycles in everything according to the Design details. The bicycle parking space is 70x70 cm in size. It is made of metal box profiles 5x2cm and anchored in the floor in 3 places. Parking spaces are finished with metal coatings and black paint. Parking spaces are installed at a distance of 120 cm. | kom/ pcs |  | 17 | 0
30. |  | Jarboli sa zastavama: Nabavka i ugradnja dva fiberglas jarbola bijele boje, visine 6m za montiranje državne zastave i zastave Glavnog grada. Jarbol je konusnog oblika, elastičan, trpi blago savijanje zbog čega je otporan na udare vjetra i ostale atmosferske uticaje. Jarbol se ne farba, zbog čega nije potrebno dalje održavanje. Materijal od kojeg se proizvodi jarbol ne provodi elektricitet i zato je nepotrebno uzemljavati ga radi zaštite od udara groma. Sistem sa unutrašnjim mehanizmom i rotirajućom glavom omogućava da se zastava rotira za 360 stepeni, što joj znatno produžava vijek trajanja, kao i samog jarbola. G nosač omogućava da zastava uvijek bude otvorena i jasno vidljiva. Anker stopa izrađena je po sistemu šarke zbog čega je polaganje jarbola na zemlju veoma jednostavno. Bravica omogućava osiguranje zastave od neovlašćenog spuštanja ili krađe. Jarbol se ugrađuje na armirano-betonskom temelju. Preporuka je da se zastava treba skinuti sa jarbola ukoliko je jačina vjetra veća od 45km/h, kako bi produžili vijek trajanja zastave. Jarboli se montiraju u betonsko postolje dimenzija 30x30cm i dubine 80cm. U cijenu pozicije ulazi i nabavka i montaža zastava. | The Masts with flags: Procurement and installation of two white fibreglass masts, 6m high, for mounting the national flag and the flag of the Capital City. The mast has a conical shape, is elastic, and allows for slight bending, which is resistant to wind blows and other atmospheric influences. The mast is not painted, so no further maintenance is required. The material from which the mast is made does not conduct electricity, so it is unnecessary to ground it to protect against lightning strikes. The system with an internal mechanism and the rotating head allows the flag to rotate 360 degrees, which significantly extends service life for flags and masts. The G holder enables the flag always to be open and visible. The anchor foot is made according to the hinge system, which makes it very easy to place the mast on the ground. The lock enables securing the flag against unauthorized lowering or theft. The mast is installed on the reinforced concrete foundation. It is recommended flag should be removed from the mast if the wind speed is great to extend the flag's lifetime of the flag. The masts are mounted in the concrete base measuring 30x30cm and 80cm deep. The price of the position includes the purchase and installation of flags. | kom/ pcs |  | 2 | 0
31. |  | Završno čišćenje terena: Završno čišćenje slobodne površine terena. Čišćenje će se platiti samo jednom, bez obzira na broj izvršenih čišćenja u toku pripreme objekta za predaju. | Final cleaning of the field: Final cleaning of the free surface of the field. Cleaning will be paid for only once, regardless of the number of cleanings performed while preparing the object for delivery. | m2 |  | 10100 | 0
VII. |  | RAZNI RADOVI | MISCELLANEOUS WORKS |  |  | Ukupno/total | 0
1.2. |  | REKAPITULACIJA - UREĐENJE TERENA | SUMMARY - LANDSCAPING
I. |  | PRIPREMNI RADOVI | PREPARATORY WORKS |  |  |  | 0
II. |  | ZEMLJANI RADOVI | EARTHWORKS |  |  |  | 0
III. |  | BETONSKI I ARMIRANO-BETONSKI RADOVI | CONCRETE AND REINFORCEMENT CONCRETE WORKS |  |  |  | 0
IV. |  | ARMIRAČKI RADOVI | REINFORCEMENT WORKS |  |  |  | 0
V. |  | BRAVARSKI RADOVI | METAL-FENSING WORKS |  |  |  | 0
VI. |  | SPORTSKA OPREMA | SPORTS EQUIPMENT: |  |  |  | 0
VII. |  | RAZNI RADOVI | MISCELLANEOUS WORKS |  |  |  | 0
1.2. |  | UKUPNO UREĐENJE TERENA | TOTAL LANDSCAPING |  |  |  | 0

## 2.2. ViK-WS and SEWERAGE
Program obrazovanja Crne Gore/ Education program of Montenegro
Predmjer - Izgradnja nove OŠ "Vladimir Nazor"/ Bill of Quantity - Construction of the new Elementary School "Vladimir Nazor" INSTALACIJE VODOVODA I KANALIZACIJE / WATER SUPPLY AND SEVAGE INSTALLATION
br/ No | predmet / subject | NASLOV | DESCRIPTION | mj.jedinica/ unit | pred.cijena u eurima/ unit price € | Količina / Quantity | Cijena u eurima (bez PDV-a) / Amount in € (excl VAT)
(a) | (b) | (c) |  | ( d ) | (e) | (f) | (g=e*f)
2.2. |  | INSTALACIJE VODOVODA I KANALIZACIJE | WATER SUPPLY AND SEVAGE INSTALLATION
|  | PREDMJER I PREDRAČUN SPOLJAŠNJIH INSTALACIJA VODOVODA I KANALIZACIJE | BILL OF QUANTITY OF EXTERNAL WATER SUPPLY AND SEWAGE INSTALLATION
I. |  | UREĐENJE TERENA - ZEMLJANI RADOVI | LANSCAPING - EARTHWORKS
1. |  | Mašinski i ručni iskop u materijalu svih kategorija za rovove za postavljanje cjevovoda. Širina iskopa dna trapeznog rova je za atmosfersku i fekalnu kanalizaciju 0.7/0.8m dok je za vodovod 0.6m. Iskopani materijal odbaciti na 1,0m od ivice rova sa jedne strane tako da jedna strana rova bude slobodna za odlaganje cijevi i ostalog potrebnog materijala za montažu cjevovoda. Kod iskopa voditi računa da dno kanala bude fino isplanirano u niveleti, a strane rova da budu pravilno odsječene. | Mechanical and manual excavation in the material of all categories for installation trenches. The width of the excavation of the bottom of the trapezoid trench is 0.7/0.8m for atmospheric and house sewage, while it is 0.6m for water supply. Discard the excavated material 1.0m from the edge of the trench on one side so that one side of the trench is free for storing pipes and other necessary materials for pipeline assembly. During the excavation, ensure that the bottom of the canal is finely levelled and that the sides of the trench are properly cut
|  | Atmosferska kanalizacija | Atmospheric sewage | m3 |  | 320 | 0
|  | Fekalna kanlizacija | House sewage | m3 |  | 200 | 0
|  | Instalacije vodovoda i hidrantska mreža | water supply and hydrant pipeline | m3 |  | 260 | 0
2. |  | Mašinski i ručni iskop u materijalu svih kategorija za postavljane opreme i formiranje objekata. | Mechanical and manual excavation in the material of all categories for installation of equipment and elements of the distribution line
|  | Separatori | Separators | m3 |  | 20 | 0
|  | Upojni rovovi | Sewage Absorption Trench | m3 |  | 250 | 0
3. |  | Nabavka, transport i ugradnja sitnozrnog pijeska za montažu cjevovoda ispod cjevovoda okolo i iznad cjevovoda. Obračun po m3. | Supply, transport and spreading of fine sand for the installation under pipelines around and above pipelines. Calculation per m3.
|  | Atmosferska kanalizacija | Atmospheric sewage | m3 |  | 107 | 0
|  | Fekalna kanalizacija | House sewage | m3 |  | 35 | 0
|  | Instalacije vodovoda i hidrantska mreža | water supply and hydrant pipeline | m3 |  | 66 | 0
4. |  | Zatrpavanje kanalskih rovova sa montiranim cjevovodom, objekta i biološkog uređaja. Zatrpavanje se vrši u slojevima debljine 30 do 40cm uz propisno nabijanje do postizanja poterbnog modula stišljivosti. Zatrpavanje se vrši ručno materijalom iz iskopa. Obračun po m3 | Backfilling of trenches with the installed pipeline, facility and microbial device. Backfilling is done in layers 30 to 40 cm thick with proper compaction until the required compressibility modulus is reached. Backfilling is done manually with material from the excavation. Calculation per m3
|  | Atmosferska kanalizacija | Atmospheric sewage | m3 |  | 213 | 0
|  | Fekalna kanlizacija | House sewage | m3 |  | 165 | 0
|  | Instalacije vodovoda i hidranstska mreža | water supply and hydrant pipeline | m3 |  | 194 | 0
|  | Separatori | Seperators | m3 |  | 20 | 0
|  | Upojni rovovi | Sewage Absorption Trench | m3 |  | 15 | 0
5. |  | Dodatni iskop za okna. Iskopi se obavljaju u materijalu u kome se vrši iskop kanalskog rova. Jediničnom cijenom je obuhvaćen sav potreban rad i materijal uključujući potrebnu pažnju oko čuvanja postojećih instalacija i eventualno potrebno podgrađivanje. Obračun po m3, uredno i kvalitetno obavljenog iskopa koji podrazumijeva odbacivanje materijala od iskopa na dovoljnu udaljenost kako isti ne bi ometao komunikaciju uz rov. | Additional excavation for the manhole. Excavations are carried out in the material where the canal trench is excavated. The unit price includes all necessary work and materials, including the required attention to protecting existing installations and any measures needed to protect the sides of the excavation. Calculation per m3 of properly performed excavation includes discarding the material from the hole at a sufficient distance so that it does not interfere with works along the trench.
|  | Atmosferska kanalizacija | Atmospheric sewage | m3 |  | 65 | 0
|  | Fekalna kanlizacija | House sewage | m3 |  | 22 | 0
|  | Vodomjerni šaht | Water gauge manhole | m3 |  | 18 | 0
6. |  | Utovar i transport viška materijala iz iskopa na gradsku deponiju sa grubim planiranjem na mjestu istovara. Količine prema tabelarnim dokaznicama.Plaćanje se vrši po m3 prevezene i isplanirane zemlje. | Loading and transporting surplus material from the excavation to the city landfill with rough planning at the unloading site. Quantities according to table calculation. Payment is made per m3 of transported and planned soil
|  | Atmosferska kanalizacija | Atmospheric sewage | m3 |  | 172 | 0
|  | Fekalna kanlizacija | House sewage | m3 |  | 57 | 0
|  | Instalacije vodovoda i hidranstska mreža | water supply and hydrant pipeline | m3 |  | 84 | 0
|  | Upojni rovovi | Sewage Absorption Trench | m3 |  | 235 | 0
I. |  | UREĐENJE TERENA - ZEMLJANI RADOVI | LANSCAPING - EARTHWORKS |  |  | Ukupno/ Total | 0
II. |  | INSTALATERSKI RADOVI I OPREMA | INSTALLATION WORKS AND EQUIPMENT
7. |  | Nabavka transport i ugradnja kanalizacionih cijevi od tvrdog polivinillhlorida (PVC) sa jednoličnim presjekom zida klase Sn8, sa zaptivnim prstenom punih zidova čvrstoće prema standardu ISO 9969 . Cijevi se ugrađuju na predhodno izrađenoj posteljici od pijeska u svemu prema detaljima iz projekta. Jediničnom cijenom je obuhvaćen sav potreban rad i materijal za potpunu i pravilnu montažu kanalizacionih cijevi. Obračun po m1 montiranih cijevi. | Procurement, transport and installation of sewer pipes made of rigid polyvinyl chloride (PVC) with a uniform cross-section of walls, Sn8 class, with a sealing ring made of solid walls, with strength according to the ISO 9969 standard. The pipes are placed on the previously made sand layer according to design details. The unit price includes all necessary works and materials for the complete and correct installation of sewer pipes. Calculation per m1 of installed pipes.
|  | DN200 atmosferska | DN200 atmospheric sewage | m1 |  | 60 | 0
|  | DN160 fekalna i atmosferska | DN160house and atmospheric sewage | m1 |  | 570 | 0
|  | DN110 atmosferska | DN110 atmospheric sewage | m1 |  | 20 | 0
8. |  | Nabavka, transport i montaža polietilenskih cevi za transport kanalizacije pod pritiskom, izrađenih od polietilena visoke gustine HDPE PE-100, nazivnog pritiska, prečnika i klase određene projektom.HDPE PE-100 cevi treba da budu proizvedene i atestirane u skladu sa EN 12201 o čemu će svedočiti DVGW sertifikat i INSTA CERT sertifikat kao obavezni prilog uz isporučene cevi. Cevi treba da budu tipa "Peštan" Arađelovac ili druge cevi ekvivalentnih karakteristika. Cijevi prednika dn110mm. Obračun po m1. | Procurement, transport and installation of polyethylene pipes for the transport of sewage under pressure, made of high-density polyethylene HDPE PE-100, nominal pressure, diameter and class determined by design. HDPE PE-100 pipes should be manufactured and certified in accordance with EN 12201, which will witness the DVGW certificate and the INSTA CERT certificate as mandatory attachments to the supplied pipes. Pipes should be of the "Peštan" Arađelovac type or other pipes with equivalent characteristics. Pipes of the diameter 110 mm. Calculation per m1. | m1 |  | 40 | 0
9. |  | Nabavka, transport i ugradnja uličnih kanala sa rešetkom tipa "TEKLA 2020-D400". Obračun po m ugrađenog kanala- rešetke. | Procurement, transportation and installation of street channels - line gullies with a grid type "TEKLA 2020-D400". Calculation per m1 of installed channel - grid. | m1 |  | 11 | 0
10. |  | Nabavka i ugradnja niskoprofilnog kanala za linijsko odvodnjavanje ACO DRAIN® Multiline V100S, prema SRPS EN 1433 i DIN 19580, sa sigurnosnim zaključavanjem rešetke bez zavrtnja tip Drainlock, napravljenog od ACO polimerbetona otpornog na dejstvo mraza i soli, sa integrisanim zaštitnim rubom od pocinkovanog čelika, sa preklopom i žljebom za jednostavno zaptivanje na mestu spoja dva kanala. Kanal je namenjen je za opterećenja do klase D400. Elementi su dužine 100cm, nominalne širine 10cm, građevinske širine 13,5cm, građevinske visine 10cm. Priključak na kanalizaciju izvesti uz pomoć tela kanala sa vertikalnim priključkom sa integrisanom gumenom spojnicom za cev DN/OD100. Element kanala sa vertikalnim izlivom je građevinske visine 11cm. Obračun po m. | Supply and installation of a low-profile channel for linear gully ACO DRAIN® Multiline V100S, according to SRPS EN 1433 and DIN 19580, with the safety locking grid without screws, type Drainlock, made of ACO polymer concrete resistant to frost and salt, with the integrated protective edge of galvanized steel, with flap and groove for easy sealing at the junction of two channels. The channel have to be intended for traffic load up to class D400. The elements are 100 cm long, 10 cm nominal width, 13.5 cm construction width, and 10 cm construction height. Connect to the sewage system by the channel body with the vertical joint and integrated rubber coupling for a pipe DN/OD100. The channel element with a vertical outlet has a height of 11 cm. Calculation per m.
|  | Multiline V100S niskoprofilni | Multiline V100S low-profile | m1 |  | 32 | 0
|  | Multiline V100S niskoprofilni sa vertikalnim izlivom DN100 | Multiline V100S low-profile with vertical outlet DN100 | m1 |  | 4 | 0
|  | čeoni poklopac | front cover | m1 |  | 6 | 0
11. |  | Rešetka linijskog odvodnjavanja ACO DRAIN®Multiline V100 Rebrasta | Line drainage grid ACO DRAIN®Multiline V100 Ribbed
|  | Nabavka rešetki za kanale za linijsko odvodnjavanje ACO Multiline V100 za klasu opterećenja B125 (saobraćaj putničkim vozilima) prema SRPS EN 1433 sa sigurnosnim zaključavanjem bez zavrtnja tip Drainlock i osiguranjem protiv podužnog pomeranja, napravljenih od livenog gvožđa, širina otvora 12mm, tip Rebrasta. Rešetka je širine 123 mm, dužine 50cm, upojne površine 371 cm²/m. Obračun po dužnom metru. | Supply of grids for linear drainage channels ACO Multiline V100 for traffic load class B125 (passenger vehicle traffic) according to SRPS EN 1433 with safety and anti-displacement (longitudinal) locking without screws type Drainlock, made of cast iron, opening width 12mm, Rib type. The grid is 123 mm wide, 50 cm long, absorbent surface of 371 cm²/m. Calculation per meter | m1 |  | 36 | 0
12. |  | Nabavka transport i ugradnja vodovodnih cijevi od polietilena visoke gustoće PEHD klase 100 za pritiske PN 10, prečnika DN 110 mm uključujući i fazonske komade od PEHD-a za horizontalnelomove cjevovoda. Cijevi se ugrađuju na predhodno izrađenoj posteljici od pijeska u svemu prema detaljima iz projekta. Jediničnom cijenom je obuhvaćen sav potreban rad i materijal za potpunu i pravilnu montažu vodovodnih cijevi od PEHD u svemu prema detaljima iz projekta i propisima za ovu vrstu radova. Obračun po m1 montiranih, ispitanih i od nadzora primljenih PEHD cijevi, klase PE-100, za radne pritiske NP 10 bara. Prečnika DN 110mm. NORMA EN-12.201-2 DIN 8072/8074 | Procurement, transport and installation of water pipes made of high-density polyethylene PEHD class 100 for pressures PN 10, diameter DN 110 mm, including shaped pieces made of PEHD for horizontal unbreakable pipelines. The pipes are installed on the previously made sand layer according to the details of the design. The unit price includes all the necessary work and materials for the complete and correct installation of PEHD water pipes in accordance with the details of the design and the regulations for this type of work. Calculation per m1 of installed, tested and approved PEHD pipes, class PE-100, for working pressures of NP 10 bar. Diameter DN 110mm. NORM EN-12.201-2 DIN 8072/8075
|  | DN110 glavni dovod i spoljašnja ph mreža | DN110 | m1 |  | 480 | 0
|  | DN110 sprinkler sistem | DN110 sprinkler system | m1 |  | 150 | 0
|  | DN32 dovod za česme | DN32 distribution for the taps | m1 |  | 5 | 0
13. |  | Nabavka transport i ugradnja potrebne opreme i vodovodne fazonerije za formiranje priključnog i vodomjernog šahta. | Procurement, transport and installation of the necessary equipment and plumbing fittings for performing the connecting and water gauge manhole.
|  | POKLOPAC DN600 400KN | MANHOLE STEEL COVER DN600 400KN | kom/pcs |  | 2 | 0
|  | VODOMJER DN80 | WATER GAUGE DN80 | kom/pcs |  | 1 | 0
|  | VODOMJER DN80/20 | WATER GAUGE DN80/20 | kom/pcs |  | 1 | 0
|  | EV VENTIL DN100 | EV VALVE DN100 | kom/pcs |  | 3 | 0
|  | EV VENTIL DN80 | EV VALVE DN80 | kom/pcs |  | 2 | 0
|  | REDUKCIJA 100/80 | REDUCTION 100/80 | kom/pcs |  | 2 | 0
|  | OP KOMAD DN100/100 | OP PIECE DN100/100 | kom/pcs |  | 1 | 0
|  | SP KOMAD DN80/300 | SP PIECE DN80/300 | kom/pcs |  | 2 | 0
|  | LP4 KOMAD DN100 | LP4 PIECE DN100 | kom/pcs |  | 1 | 0
|  | NEPOVRATNI VENTIL DN80 | IRREVERSIBLE VALVE DN80 | kom/pcs |  | 2 | 0
|  | HVATAČ NEČISTOĆA DN100 | DIRT CATCHER DN100 | kom/pcs |  | 1 | 0
|  | TULJAK DN110/100 | STUB END DN110/100 | kom/pcs |  | 3 | 0
|  | UNIVERZALNA SPOJNICA DN250 | UNIVERSAL COUPLING DN250 | kom/pcs |  | 2 | 0
|  | OP KOMAD DN250/100 | OP PIECE DN250/100 | kom/pcs |  | 1 | 0
14. |  | Nabavka transport i ugradnja nadzemnog protivpožarnog hidranta DN100 sa kompletnom hidrantskom garniturom. I jednokrilnog hidrantskog ormara sa pratećom opremom: - crijevo fi 52mm/15m - 2kom - mlaznica sa ručkom fi52 - 2kom - kluč za nadzemni hidrant - 1 kom - ključ C - 1kom - ključ ABC - 1kom | Procurement, transport and installation of the overhead fire hydrant DN100 with the complete hydrant set and the single-wing hydrant cabinet with the following equipment: - hoseØ 52mm/15m - 2 pcs - nozzle with handleØ52 - 2 pcs - key for overhead hydrant - 1 pc - key C - 1 pc - key ABC - 1 pc | kom/pcs |  | 4 | 0
15. |  | SEPARATOR LAKIH NAFTNIH DERIVATA SA BYPASS-om ACO OLEOPATOR-BYPASS-P-X-FST NS3/15 ST300 | SEPARATOR OF LIGHT PETROLEUM DERIVATIVES WITH BYPASS ACO OLEOPATOR-BYPASS-P-X-FST NS3/15 ST301
|  | Nabavka i ugradnja separatora lakih tečnosti od centrifugalo livenog polietilena. Separator mora biti konstruisan, izrađen i testiran prema SRPS EN 858, nazivne veličine NS3 (protoka 3l/s) dok je ukupni protok Qmax = 15 l/s, sa integrisanim taložnikom kapaciteta 381 litara. Separator mora imati efikasnost izdvajanja lakih naftnih derivata I klase - lakih naftnih derivata u izlaznoj vodi do 5mg/l. Separator ima zapreminu izdvojenih lakih tečnosti cc. 240 litara, dok je ukupna zapremina cc. 731 litara. Uliv i izliv iz separatora su DN 200 od PEHD cevi. Dubina ulivne cevi, mereno od kote poklopca do kote dna cevi uliva T= 0,48 m do 2,16 m (tačnu dubinu cevi na ulivu treba definsati pre naručivanja separatora). Separator se isporučuje sa poklopcem prema SRPS EN 124 klase nosivosti A15, svetlog otvora prečnika 600mm, sa natpisom "SEPARATOR". Obračun po komadu puštenog u rad separatora. | Procurement and installation of light liquid separators made of centrifugally cast polyethylene. The separator have to be designed, manufactured and tested according to SRPS EN 858, nominal size NS3 (flow rate three l/s), and the total flow rate is Qmax = 15 l/s, with an integrated precipitator with a capacity of 381 litres. The separator must have the efficiency of extracting light petroleum derivatives of class I - light petroleum derivatives in the output water up to 5mg/l. The separator has a volume of separated light liquids cc. 240 litres, while the total volume is cc. 731 litres. The inlet and outlet from the separator are DN 200 PEHD pipes. The depth of the inlet pipe, measured from the height of the cover to the height of the bottom of the inlet pipe T= 0.48 m to 2.16 m (the exact depth of the pipe at the inlet should be defined before ordering the separator). The separator is delivered with the cover according to SRPS EN 124, load class A15, with a clear opening of 600 mm diameter, with the inscription "SEPARATOR". Calculation per piece of the separator put into operation. | kom/pcs |  | 1 | 0
16. |  | SEPARATOR LAKIH NAFTNIH DERIVATA SA BYPASS-om ACO OLEOPATOR-BYPASS-P-X-FST NS6/30 ST600 ili ekvivalentnih karakteristika | SEPARATOROF LIGHT PETROLEUM DERIVATIVES WITH BYPASS ACO OLEOPATOR-BYPASS-P-X-FST NS6/30 ST600
|  | Nabavka i ugradnja separatora lakih tečnosti od centrifugalo livenog polietilena. Separator mora biti konstruisan, izrađen i testiran prema SRPS EN 858, nazivne veličine NS6 (protoka 6l/s) dok je ukupni protok Qmax = 30 l/s, sa integrisanim taložnikom kapaciteta 702 litara. Separator mora imati efikasnost izdvajanja lakih naftnih derivata I klase - lakih naftnih derivata u izlaznoj vodi do 5mg/l. Separator ima zapreminu izdvojenih lakih tečnosti cc. 235 litara, dok je ukupna zapremina cc. 1036 litara. Uliv i izliv iz separatora su DN 250 od PEHD cevi. Dubina ulivne cevi, mereno od kote poklopca do kote dna cevi uliva T= 0,455 m do 2,135 m (tačnu dubinu cevi na ulivu treba definsati pre naručivanja separatora). Separator se isporučuje sa poklopcem prema SRPS EN 124 klase nosivosti B125, svetlog otvora prečnika 600mm, sa natpisom "SEPARATOR". Obračun po komadu puštenog u rad separatora. | Procurement and installation of light liquid separators made of centrifugal cast polyethilene. The separator must be designed, manufactured and tested according to SRPS EN 858, nominal size NS6 (flow 6l/s) while the total flow is Kmax = 30 l/s, with the integrated clarifier with a capacity of 702 litres. The separator must have the efficiency of extracting light petroleum derivatives of class I - light petroleum derivatives in the output water up to 5mg/l. The separator has a volume of separated light liquids cc. 235 litres, while the total volume is cc. 1036 litres. The inlet and outlet from the separator are DN 250 PEHD pipes. The depth of the inlet pipe, measured from the height of the cover to the height of the bottom of the inlet pipe T= 0.455 m to 2.135 m (the exact depth of the pipe at the inlet should be defined before ordering the separator). The separator is delivered with the cover according to SRPS EN 124, load class B125, with a clear opening of 600 mm diameter, with the inscription "SEPARATOR". Calculation per piece of the separator put into operation. | kom/pcs |  | 1 | 0
17. |  | Bunar za navodnjavanje | Irrigation well
|  | Bušenje bunara 220mm sa ugradnjom cevi 160mm | Drilling a well 220 mm with the installation of a pipe 160 mm | m1 |  | 35 | 0
|  | Ispiranje bunara. Pausalno 4h. | Flushing of the well. Lump sum 4h.. | paus/LS |  | 1 | 0
|  | CAPRARI bunarska pumpa 6 7,5kw. | CAPRARI well pump 6 7.5kw. | kom/pcs |  | 1 | 0
|  | Elektro ormar sa frekventnim regulatorom snage 7,5kw sa odvodnicima prednapona asimetrijom faza I i transmiterom pritiska 10 | Electrical cabinet with 7.5kw power frequency regulator with phase I asymmetry pre-voltage arresters and pressure transmitter 10 | kom/pcs |  | 1 | 0
|  | Energetski ormar za pumpu | Power supply cabinet for the pump | kom/pcs |  | 1 | 0
|  | Usponski cjevovod od pumpe do šahta-kućice. | Distributive pipeline from the pump to the well's manhole | m1 |  | 35 | 0
|  | Ekspanziona posuda 200l | Expansion tank 200 l | kom/pcs |  | 1 | 0
|  | Transmiter pritiska | Pressure transmitter | kom/pcs |  | 1 | 0
|  | Sajla za pumpu fi8 | Pump cable fi9 | m1 |  | 35 | 0
|  | Glava bunara | The head of the well | kom/pcs |  | 1 | 0
|  | Usluga montaže i puštanja u rad | Installation and commissioning service | kom/pcs |  | 1 | 0
|  | Filtracija vode | Water filtration | kom/pcs |  | 1 | 0
18. |  | Nabavka transport i ugradnja buster pumpe za atmosferske vode sa podruma (stepenišnih tribina). | Supply, transport and installation of the booster pump for atmospheric waste water from the basement (grandstands)
|  | WILO REXA FIT V05DA-222/EAD1-2- T0025-540-O - 6064589 | WILO REXA FIT V05DA-222/EAD1-2- T0025-540-O - 6064590 | kom/pcs |  | 2 | 0
|  | WILO MEHANIZAM ZA VJEŠANJE SUSPENSION DEVICE DN50/2RK SB - 6070146 | WILO SUSPENSION DEVICE DN50/2RK SB - 6070147 | kom/pcs |  | 2 | 0
|  | WILO VENTIL NEPOVRATNI N-RE-DEV DN50 PN10 Z GG25 CPL. - 2017166 | WILO IRREVERSIGLE VALVE N-RE-DEV DN50 PN10 Z GG25 CPL. - 2017167 | kom/pcs |  | 2 | 0
|  | WILO OVALNI ZASUN GATE VALVE DN50 PN16 GG25 CPL. - 2017160 | WILO GATE VALVE DN50 PN16 GG25 CPL. - 2017161 | kom/pcs |  | 2 | 0
|  | WILO VOÐICE INOX 26,9x2; 6m - 2976454 | WILO GUIDES INOX 26,9x2; 6m - 2976455 | kom/pcs |  | 4 | 0
|  | WILO LANAC CHAIN+2SHACKLES 5M 1.4401/316/INOX - 6063136 | WILO CHAIN+2SHACKLES 5M 1.4401/316/INOX - 6063137 | kom/pcs |  | 2 | 0
|  | WILO W-CTRL-MS-L-2X4KW-DOL 2539745 | WILO W-CTRL-MS-L-2X4KW-DOL 2539746 | kom/pcs |  | 1 | 0
|  | WILO FLOAT SW.WA65(PSN-O)10M+VP. 503211893 | WILO FLOAT SW.WA65(PSN-O)10M+VP. 503211894 | kom/pcs |  | 3 | 0
19. |  | Nabavka, transport i ugradnja česme za pijaću vodu sa svim potrebnim elementima za spajanje na dovodni cjevovod dn32. Česma prefabrikovana, laka betonska po izboru projektanta eneterijera. Obračun po kompletu. | Supply, transport and installation of the tap for drinking water with all the necessary elements for connection to the supply pipeline dn32. The prefabricated, lightweight concrete base have to be chosen by the interior designer. Calculation per set. | kom/pcs |  | 2 | 0
II. |  | INSTALATERSKI RADOVI I OPREMA | INSTALLATION WORKS AND EQUIPMENT |  |  | Ukupno/Total | 0
III. |  | BETONSKI RADOVI ARMIRAČKI I RAZNI RADOVI | CONCRETE, REINFORCEMENT AND MISCELLANEOUS WORKS
20. |  | Nabavka, transport i ugradnja vodonepropusnog betona MB 30 prema detaljima iz porjekta. Jediničnom cijenom je obuhvaćen sav potreban rad i materijal uključujući i potrebnu oplatu i betonsko željezo. Radove izvesti u svemu prema propisima za ovu vrstu radova i detaljima iz projekta. Obračun po m3 ugrađenog betona. | Supply, transport and pouring of waterproof concrete MB 30 according to the details of the design. The unit price includes all the necessary work and materials, including the necessary formwork and reinforcement. Perform the work in accordance with the regulations for this type of work and details from the design. Calculation per m3 of poured concrete
|  | Atmosferska kanalizacija | Atmospheric sewage
|  | Donja ploča slivnika i revizionih okana | The bottom plate of the gully and inspection manholes | m3 |  | 2.04 | 0
|  | Kineta | Bench and invert of the channel | m3 |  | 3.9 | 0
|  | Gornja ploča i vijenac | Top plate with cornice | m3 |  | 6.9 | 0
|  | Fekalna kanalizacija | House sewage
|  | Donja ploča revizionih okana | The lower plate of inspection manholes | m3 |  | 2.04 | 0
|  | Kineta | Bench and invert of the channel | m3 |  | 3.9 | 0
|  | Gornja ploča i vijenac | Top plate with cornice | m3 |  | 4.14 | 0
|  | Priključni i vodomjerni šaht | Connecting and water gauge manhole | m3 |  | 9 | 0
|  | Podložna ploča za separatore | Base plate for separators | m3 |  | 1.1 | 0
|  | Upojni bunari | Absorption wells | m3 |  | 5.5 | 0
21. |  | Nabavka, transport i ugradnja armirano-betonskih cijevi profila 1000 mm dužine L=1000 mm.Cijevi se ugrađuju u reviziono slivničko okno tako da se njime formira tijelo okna. Jedininičnom cijenom obuhvaćen je sav potreban rad i materijal za ugradnju cijevi uključujući potrebna štemovanja za penjalice, krpljenje betonskih cijevi nakon ugradnje penjalica,potrebna skraćenja cijevi, temeljenje cijevi u dno i kinetu i sve ostale radove kojima se obezbeđuje potpuno formiranje zida okna od armirano-betonskih cijevi. Obračun po komadu ugrađenih armirano-betonskih cijeviu slivničko ili reviziono okno. | Supply, transport and installation of reinforced concrete pipes with a diameter of 1000 mm, and length L=1000 mm. The unit price includes all the necessary work and material for the installation of the pipes, including the necessary cuttings for the climbers, the patching of the concrete pipes after the installation of the climbers, the necessary shortening of the pipes, the foundation of the pipes in the bottom and preparation of benches and inverts of channel including other works that ensure the completion of the manhole wall from reinforced concrete pipes. Calculation per piece of installed reinforced concrete pipes in the gully or inspection manhole.
|  | Atmosferska kanalizacija | Atmospheric sewage | kom/pcs |  | 12 | 0
|  | Fekalna kanlizacija | House sewage | kom/pcs |  | 10 | 0
22. |  | Zidanje zidova upojnih bunara betonskim blokovima 40x20x20 u cementnom malteru sa ostavljanjem prostorom između blokova zbog boljeg upijanja okolnog tla. U cijenu je uračunat sav potreban rad i materijal . Obračun po m2 ozidanog zida. | Masonry of the walls of absorption wells with concrete blocks 40x20x20 in cement mortar, leaving space between the blocks for better absorption of the surrounding soil. All necessary work and materials are included in the price. Calculation per m2 of the brick wall. | m2 |  | 150 | 0
23. |  | Nabavka, transport i ugradnja jednodjelnih slivničkih rešetki od nodularnog liva (prema standardu EN124) sa zglobnom vezom rešetke i rama.Rešetke su pravougaonog oblika, dimenzija svijetlog otvora 600x600mm za opterećenja od 400kN. Jediničnom cijenom je obuhvaćen sav potreban rad i materijal za kvalitetnu ugradnju slivnika u skladu sa detaljima iz projekta. Obračun po komadu ugrađenog i za AB venac ankerisanog zaštićenog od korozije slivnika. | Supply, transport and installation of a one-piece drain grid made of nodular cast iron (according to the EN124 standard) with a hinged connection of the grid and frame. The grids are rectangular, and the dimensions of the clear opening are 600x600mm for traffic loads of 400kN. The unit price includes all the necessary work and materials for the installation of the gullies with details from the design. Calculation per piece of corrosion-protected, installed, and anchored gully to RC cornice | kom/pcs |  | 6 | 0
24. |  | Nabavka, transport i ugradnja poklopaca sa ramom od nodularnog liva (prema standardu EN124). Poklopci su okrugli, svetlog otvora prečnika600 mm za opterećenja od 400kN i zglobnom vezom rama i poklopcai gumenim dihtungom za nalijeganje poklopca na ram i mehanizmom za zaključavanje. Jediničnom cijenom je obuhvaćen sav potreban rad i materijal za kvalitetnu ugradnju poklopaca u skladu sa detaljima iz projekta. Obračun po komadu ugrađenog i zaštićenog od korozije poklopca. | Supply, transport and installation of covers with a frame made from nodular cast iron (according to the EN124 standard). The covers are round, with a clear opening of 600 mm in diameter for traffic loads of 400kN, with the articulated connection of the frame and cover, the rubber gasket for fitting the cover on the frame, and the locking mechanism. The unit price includes all necessary work and materials for the installation of covers in accordance with the details from the design. Calculation per piece of protected from corrosion and installed cover
|  | Atmosferska kanalizacija (vode sa krova) | Atmospheric sewage (water from the roof) | kom/pcs |  | 4 | 0
|  | Fekalna kanlizacija | House sewage | kom/pcs |  | 6 | 0
|  | Upojni bunari | Absorption wells | kom/pcs |  | 2 | 0
25. |  | Nabavka, transport i ugrađivanje liveno-gvozdenih penjalica u šahtovima revizionim oknima. Penjalice se ugrađuju u svemu prema detaljima projekta. Obračun po komadu ugrađene penjalice. | Procurement, transport and installation of cast-iron climbers in inspection manholes. Climbers are installed according to the details of the design. Calculation per piece of installed climber
|  | Atmosferska kanalizacija | Atmospheric sewage | kom/pcs |  | 36 | 0
|  | Fekalna kanalizacija | House Sewage | kom/pcs |  | 33 | 0
|  | Vodovod | Water pipe | kom/pcs |  | 8 | 0
|  | Upojni bunari | Absorbent wells | kom/pcs |  | 20 | 0
III. |  | BETONSKI RADOVI ARMIRAČKI I RAZNI RADOVI | CONCRETE, REINFORCEMENT AND MISCELLANEOUS WORKS |  |  | Ukupno/ Total | 0
|  | PREDMJER I PREDRAČUN UNUTRAŠNJIH INSTALACIJA VIK | BILL OF QUANTITY INTERNAL WATER SUPPLY AND SEWAGE INSTALLATION
IV. |  | INSTALACIJE VODOVODA | WATER SUPPLY INSTALLATION
26. |  | Nabavka, transport i montaža pocinčanih vodovodnih cijevi i fazonskih komada sa svim potrebnim fitinzima za radne pritiske 10 bara. Pocinčane cijeve su dužine do po 6m sa mogućnošću sječenja na po 3m. Sve pocinčane razvode hidrantske mreže kao i vidni plafonski razvod i sve ostale vidne razvode zastititi sa “plamafleks” cijevima. Vertikale i zidne razvode , tj. cijevi koje se razvode šlicevima kroz zidove zaštititi “FILC” trakama. Zvučno izolovati cijevi kroz konstrukciju, sa oblagajnem cijevi staklenom ili mineralnom vunom, filcom ili drugim pogodnim materijalom.Obračun po m' ugrađene pocinčane cijevi. | Supply, transport and installation of galvanized water pipes and fittings for working pressures of 10 bar. Galvanized pipes are up to 6 m long, possibly cutting them to 3 m. Protect all galvanized distributions of the hydrant network, the visible ceiling distribution and all other visible distributions with "plamaflex" pipes. Vertical and wall distributions, i.e. pipes distributed through the walls along the cuts, must be protected with "FILC" tapes. Acoustically insulate the pipes through the construction with glass or mineral wool, felt or other suitable material. Calculation per m' of installed galvanized pipe
|  | prečnika Ø50 | diameter Ø50 | m1 |  | 36 | 0
|  | prečnika Ø65 | diameter Ø65 | m1 |  | 160 | 0
27. |  | Nabavka, transport do gradilišta i ugradnja plastičnih PP-R vodovodnih cijevi i fazonskih komada za unutrašnji vodovod za radni pritisak 10 bara. Obračun je po m', cijenom je obuhvaćeno i štemovanje i krpljenje oštećenih površina, prodori kroz konstrukciju koji nisu posebno obračunati, ugrađivanje zaštitinih cijevi na prolazima kroz konstrukciju i zatvaranje svih prodora. Cijevi adekvatno zaštititi ´plamafleks´ izolacijom i propisno ispitati. Prečnici DN označeni u grafičkim prilozima pretstavljaju unutrašnji prečnik plastične vodovodne cijevi. Obračun po m' ugrađene cijevi. | Supply, transport to the construction site and installation of plastic PP-R water pipes and fittings for internal water supply for a working pressure of 10 bar. The calculation is per m'; the price includes cutting and patching of damaged surfaces, penetrations through the structure that are not separately calculated, installing protective pipes on passages through the structure, and closing all penetrations. Protect pipes with plamaflex insulation and properly test them. The DN diameters marked in the graphical documentation represent the inner diameter of the plastic water pipe. Calculation per m' of installed pipe
|  | DN50 | DN50 | m1 |  | 6.6 | 0
|  | DN40 | DN40 | m1 |  | 170.5 | 0
|  | DN32 | DN32 | m1 |  | 46.2 | 0
|  | DN25 | DN25 | m1 |  | 204.6 | 0
|  | DN20 | DN20 | m1 |  | 1240.8 | 0
28. |  | Nabavka i montaža ravnih propusnih ventila sa hromiranom kapom i rozetnom (centralnih) za polipropilenske cevi. DN20/Ø 1/2" | Supply and installation of flat permeable valves with chrome cap and rosette (central) for polypropylene pipes. DN20/Ø 1/2" | kom/pcs |  | 32 | 0
29. |  | Nabavka transport i montaža propusnih ventila sa ispustom sa svim spojnim elementima. Montaža u dnu vertikale. Obračun po komadu. | Supply, transport and installation of permeable valves with the discharge with all connecting elements. Installation in the bottom of the vertical. Calculation per piece.
|  | DN40 | DN40 | kom/pcs |  | 4 | 0
|  | DN20 | DN20 | kom/pcs |  | 2 | 0
30. |  | Nabavka, transport i montaža PPR propusnih ventila sa ukrasnom kapom . Ugradnja ventila za umivaonike i sudopere, za toplu i hladnu vodu. Obračun po komadu ugrađenog ventila | Supply, transport and installation of PPR permeable valves with a decorative cap. Installation of valves for wash basins and kitchen sinks, for hot and cold water. Calculation per piece of installed valve
|  | DN20/Ø 1/2" | DN20/Ø 1/2" | kom/pcs |  | 180 | 0
31. |  | Nabavka, transport i montaža protivpožarnih hidranata Ø 50mm koji se sastoje iz sljedećih djelova : hidrantski ormarić od dekapiranog čeličnog lima veličine 50x50x14cm, crijevo od trevire Ø 50mm dužine 15m, mesingani ventili Ø50mm, mesingana mlaznica za crijevo Ø 32mm, kućište hidranta je fabrički zaštićeno temeljnom bojom i lakirano crvenim lakom sa oznakom H na vratancima. Vratanca kućišta moraju biti osigurana plombom. Ormarić za protivpožarne hidrante ugradjuju se u prethodno obradjene niše u zidu, tako da dno ormara bude na visini 150cm od poda. Obračun po kom. | Supply, transport and installation of fire hydrants Ø 50mm, which consist of the following elements: The firebox, which is made of sheet steel size 50x50x14cm, 15m long Ø 50mm hose, Ø50mm brass valves, and Ø 32mm brass nozzle for the hose, the firebox is factory protected with a primer and painted with red varnish with the H mark on the doors. The doors of the housing must be secured with a seal. The firebox is installed in previously performed niches in the wall so that the bottom of the box is 150 cm from the floor. Calculation per piece | kom/pcs |  | 16 | 0
32. |  | Nabavka, montaža i puštanje u rad postrojenja za povećanje pritiska karakteristika proticaj Q=5l/s, H=25m. U cijenu su uračunati prateći ventili kao i komplet montaža i povezivanje na elektro instalacije. | Supply, assembly and commissioning of the station for increasing the pressure with the following characteristics: flow K=5l/s, H=25m. The price includes valves, the assembly set, and electrical installation connections | kom/pcs |  | 1 | 0
33. |  | Nabavka, montaža i puštanje u rad postrojenja za povećanje pritiska karakteristika proticaj Q=5l/s, H=25m. U cijenu su uračunati prateći ventili kao i komplet montaža i povezivanje na elektro instalacije. | Supply, assembly and commissioning of the station for increasing the pressure with the following characteristics: flow K=5l/s, H=25m. The price includes valves, the assembly set, and electrical installation connections | kom/pcs |  | 1 | 0
34. |  | Ispitivanje montirane vodovodne mreže na vodoizdržljivost prema datim uputstvima. Potrebnu količinu vode za ispitivanje obezbeđuje izvođač. Obračun po m' ispitanog cjevovoda. | Testing the installed water supply distribution pipeline for water tightness of connections, according to instructions. The required amount of water for testing is provided by the contractor. Calculation per m' of the tested pipeline. | m1 |  | 1 | 0
IV. |  | INSTALACIJE VODOVODA | WATER SUPPLY INSTALLATION |  |  | Ukupno/Total | 0
V. |  | INSTALACIJE FEKALNE KANALIZACIJE | HOUSE SEWAGE INSTALLATION
35. |  | Nabavka, transport i ugradnja niskošumnih troslojnih kanalizacionih cevi i fitinga za unutrašnje instalacije, proizvedenih prema EN 1451 od polipropilena blok-kopolimera (PP-C) ojačanog sa mineralnim aditivima, sa spoljašnjim plavim i unutrašnjim belim slojem, i povećane absorbcije buke, a u svemu prema projektovanim prečnicima i datoj specifikaciji. Prateći sistem fitinga treba da bude ojačan u delu spojnice, sa dilatacionim distancerima i markerima za određivanje ugla rotacije fitinga i isporučen u zaštitnom PE pakovanju. Niskošumne cevi i fiting moraju da su testirane prema EN 14366 i DIN 4109 i da zadovolje zahteve minimalne zvučne izolacije od 12 dB(A), što dokazuje Fraunhofer-ov izveštaj o ispitivanju uz isporučene cevi. Radove izvesti u svemu prema tehničkim propisima za predviđenu vrstu cevi, odnosno u skladu sa zahtevima EN 12056 i SRPS ENV 13801, na način koji je predvideo proizvođač cevi i u skladu sa uputstvima Nadzornog organa. Obračun po metru dužnom cijevi. | Supply, transport and installation of low-noise three-layer sewer pipes and fittings for internal installations, manufactured according to EN 1451 from polypropylene block-copolymer (PP-C); reinforced with mineral additives, external side of walls is blue and internal white, with increased noise absorption, according to designed diameters and specification. The fitting system should be reinforced in the coupling part, with expansion spacers and markers for determining the angle of rotation of the fitting and delivered in the protective PE package. Low-noise pipes and fittings must be tested according to EN 14366 and DIN 4109 and fulfill the minimum sound insulation requirements of 12 dB(A), checked and proven by the Fraunhofer test report, submitted with the delivered pipes. The work must be carried out according to the technical regulations for the intended type of pipe, i.e. in accordance with the requirements of EN 12056 and SRPS ENV 13801, in the manner foreseen by the pipe manufacturer and in accordance with the instructions of the Supervisor Authority. Calculation per meter of pipe
|  | Ø160mm | Ø160mm | m1 |  | 52.8 | 0
|  | Ø110mm | Ø110mm | m1 |  | 248.6 | 0
|  | Ø75mm | Ø75mm | m1 |  | 245.3 | 0
|  | Ø50mm | Ø50mm | m1 |  | 165 | 0
36. |  | Nabavka transport i montaža tačkastog slivnika sa rešetkom od nerđajućeg čelika. Slivnik je sa demontažnim sifonom za miris sa opciom sifonskog uloška protiv isparavanja vode Obračun po komadu ugrađenog slivnika. | Supply, transportation and installation of a point drain with a stainless steel toilet trap (gully). The drain has a removable siphon for the smell with the option of the siphon insert against water evaporation. Calculation per piece of the installed trap.
|  | Ø50mm-mokri čvorovi | Ø50mm-toilets | kom/pcs |  | 16 | 0
37. |  | Nabavka , transport i montaža revizionih komada sa vratancima u dnu vertikala. Obračun po komadu. | Supply, transport and installation of inspection pieces with doors at the bottom of the vertical pipe. Calculation per piece
|  | DN75/110 | DN75/110 | kom/pcs |  | 28 | 0
38. |  | Nabavka transport raznošenje i montaža ventilacionih kapa-glava od PVC-a. Obračun po komadu. | Supply, transport, distribution and installation of PVC ventilation hoods. Calculation per piece.
|  | ventilacione kape Ø110mm | ventilation hoods Ø110mm | kom/pcs |  | 15 | 0
|  | ventilacione kape Ø160mm | ventilation hoods Ø160mm | kom/pcs |  | 4 | 0
39. |  | Nabavka transport i montaža cijevnog dozračnika za vertikale koje ne mogu da izađu na krov radi ovazdušenja fekalne kanalizacije. Iobavezno ostaviti otvor u spuštenom plafonu radi ventilisanja istog u dijelovima gdje je predviđen dozračnik. Priključak na cijevi dn75mm. | Supply, transport and installation of the pipe aerator for vertical sewage pipes that cannot go to the roof for house sewage ventilation. Leaving an opening in the suspended ceiling for ventilation in the parts where the pipe aerator is provided is mandatory. Connection to pipe dn75mm | kom/pcs |  | 8 | 0
40. |  | Nabavka, transport i ugradnja mini vent dozračnika za montažu ispod umivaonika na mjestima gdje je predaleko odušak fekalne kanalizacije. Obračun po komadu. | Procurement, transport and installation of the mini vent aerator for installation under the sink in places where the house sewage vent is too far away. Calculation per piece | kom/pcs |  | 4 | 0
41. |  | Nabavka i ugradnja samostojećeg prepumpnog uređaja tipa Muli-Star DDP sa plietilenskim tankom i dve pumpe, 400V, 50Hz, IP 68 zaštita. Namenjene za crne otpadne vode posle separatora masti. Pneumatski nivometar sa kontrolisanje nivo otpadne vode u tanku sa potopljenom cevi. Mini kompresor za ubacivanje vazduha u potoplenu cev nivometra - specijalizovano posle separatora masti. Postrojenje poseduje radne protiv povratne ventile i ventil na potisu radi servisiranja. - korisne zapremina tanka zavisno od mesta uliva za od 95 do 165 l - Ulivi DN100/DN150 - masa praznog uređaja 108kg - potisni vod DN100 (spoljni prečnik 108 – 114.3 mm) - isporučuje se sa automatikom i UKO/UTO priključkom 32A | Procurement and installation of the free-standing pre-pumping device of the Muli-Star DDP type with the polyethylene tank and two pumps, 400V, 50Hz, IP 68 protection. The device is predicted to black waste water after the grease separator. Pneumatic level meter with checking of the wastewater level in the tank with the submerged pipe. Mini compressor for injecting air into the submerged pipe of the level meter - specialized after the grease separator. The plant has active irreversible valves and the pressure pipeline valve for servicing. - the effective volume of the tank, depending on the place of inflow, from 95 to 165 l - DN100/DN150 inlets - the weight of the empty device is 108 kg - pressure pipeline DN100 (outer diameter 108 – 114.3 mm) - delivered with automatic transmission and UKO/UTO connection 32A
|  | Muli-Star DDP 2.1 prepumpno postrojenje iza separatora masti P1/P2 = 2 x 1.83/1.5kW I = 5A, POTIS DN100 | Muli-Star DDP 2.1 pre-pumping plant behind grease separator P1/P2 = 2 x 1.83/1.5kW I = 5A, PRESSURE PIPELINE DN100 | kom/pcs |  | 1 | 0
42. |  | Ispitivanje komplet kanalizacione mreže na vodoodrživost i prohodnost. Poslije ispitivanja, cijevi i slivnike zaštititi sa cijevnim čepovima i slojem betona od fizičkog oštećenja . Obracun po m' ispitane mreže. | Testing of the complete sewage installation for water tightness and passability. After testing, protect pipes and pipe plugs (gullies) with the layer of concrete from physical damage. Calculation per m' of the tested pipeline. | m1 |  | 711.7 | 0
V. |  | INSTALACIJE FEKALNE KANALIZACIJE | HOUSE SEWAGE INSTALLATION |  |  | Ukupno | 0
VI. |  | SANITARNI PRIBORI | SANITARY EQUIPMENT AND ACCESSORIES
43. |  | Nabavka transport i montaža, konzolne WC šolje I klase sa niskomontažnim ugradnim vodokotlićem sa ugaonim ventilom i vezom, kao GEBERIT ili slično. Poklopnu dasku za WC šolju raditi sa okvirom od visoko kvalitetne plastike. Pored šolje isporučiti držač za toaletni papir postavljen lijevo ili desno od šolje na visini oko 80cm i četku za čišćenje wc šolje. Sve u kompletu prema opisu. Obračun po kompletu. | Supply, transport, and install wall-hung toilets first-class, with low-mounted built-in concealed cisterns with corner valves and connections to the distributive pipeline, like GEBERIT or similar. The toilet seats should be made with a frame made of high-quality plastic. Next to the toilet, install the holder for toilet paper, placed to the left or right of the toilet, at the height of about 80 cm and the brush for cleaning the toilet bowl. All set according to the description. Calculation per set | komplet/ set |  | 34 | 0
44. |  | Nabavka transport i montaža, konzolne WC šolje za osobe sa posebnim potrebama., zajedno sa daskom za sedenje, visine od 45-50cm. Uz WC šolju montirati dva držača za ruke dužine 90cm, postavljena na zid u rasponu visine od 80-90cm iznad površine poda. Najmanje jedan držač za ruke mora biti preklopni i to obavezno onaj sa pristupačne strane WC šolje, a drugi može biti fiksno pričvršćen na zid. Udaljenost prednje ivice WC šolje od zida najmanje 65cm. Pokretač uređaja za ispuštanje vode u WC šolju postavljen je na visini od 70cm iznad površine poda ili izvedeno senzorsko ispuštanje vode u WC šolju. Pored šolje isporučiti držač za toaletni papir postavljen levo ili desno od šolje na visini oko 50cm i četku za wc šolju. Obračun po kompletu. | Supply, transport, and install wall-hung toilet bowls for people with disabilities and toilet seats. The installation height is 45-50 cm above the floor surface. Along with the toilet, on both sides, install handrails 90cm long, at 80-90cm above the floor surface. At least one handrail must be foldable and must be the one on the accessible side of the toilet bowl, and the other can be fixed to the wall. The distance between the front edge of the WC bowl from the wall is at least 65 cm. The device's handle for draining water into the toilet bowl is placed 70 cm above the floor surface, or the sensor discharge of water into the toilet bowl is performed. Next to the bowl, install the holder for toilet paper placed to the left or right, at about 50 cm above the floor surface and the brush for the toilet bowl. Calculation per set. | komplet |  | 2 | 0
45. |  | Nabavka i montaža porcelanskih umivaonika vrhunskog kvaliteta I klase, bijele boje sa pripadajućom galanterijom . Umivaonik montirati na visini 80 cm od kote gotovog poda i pričvrstiti na zid pomoću vijaka M8. Umivaonik je opremljen sa poniklovanim sifonom , čepom i rozetnom. Na umivaonik montirati odgovarajuću stojeću jednoručnu bateriju za toplu i hladnu vodu sa poniklovanim priključnim cevima 3/8” i ugaonim ventilima Ø15mm, izlivom i perlatorom Ø15mm, visokog kvaliteta . Obračun po kompletu. | Supply and installation of first-class quality porcelain washbasins, white colour with necessary accessories. Install the washbasin at 80 cm from the height of the finished floor and fix it to the wall with M8 screws. The basin is equipped with a nickel-plated siphon, cap and rosette. On the washbasin install the standing tap - single-lever basin mixer for hot and cold water, with nickel-plated connection pipes 3/8" and corner valves Ø15mm, spout and aerator Ø15mm, high quality. Calculation per set | komplet/ set |  | 86 | 0
46. |  | Nabavka transport i ugradnja konzolnog umivaonika za osobe sa posebnim potrebama. Širina umivaonika najmanje 50 cm, a postavlja se na visini od 80cm, sa sifonom smeštenim u ili uz zid. Na umivaonik montirati odgovarajuću jednoručnu slavinu ili slavinu sa ugrađenim senzorskim otvaranjem i zatvaranjem vode. Uz umivaonik ugraditi sanitarnu garnituru/galanteriju /koju sačinjavaju : držač peškira pričvršćen na zid , držač postaviti na zidu na visini 75cm od poda, sa leve ili desne strane umivaonika na razmaku od 10cm od bočnog ruba . Iznad umivaonika montirati nagnuto, zaokretno ogledalo postavljeno donjom ivicom na visinu od 100cm. Vešalicu za odecu montirati na visini od 120cm. Obračun po kompletu. | Supply, transport and installation of the washbasin for people with disabilities. The width of the basin is at least 50 cm, and it is placed at the height of 80 cm, with the siphon placed in or against the wall. Mount a suitable tap - single-lever washbasin mixer or the mixer with a sensor for opening and closing the water. Next to the washbasin, install the sanitary accessories: towel holder attached to the wall, at the height of 75 cm from the floor, on the left or right side of the basin at a distance of 10 cm from the side edge. Above the washbasin, install an inclined, swivelling mirror placed with the lower edge at the height of 100 cm. Finally, install the clothes hanger at the height of 120 cm. Calculation per set | komplet/ set |  | 2 | 0
47. |  | Nabavka, transport i ugradnja trokadera sa rešetkom. Keramički bijli trokadero, odvod u podu -simplon veza. Obračun po komadu. | Procurement, transport and installation of a trocadero with a grid. Ceramic white trocadero, drain in the floor - ''simplon'' connection. Calculation per piece | komplet/ set |  | 1 | 0
48. |  | Nabavka i montaža tuš baterije za toplu i hladnu vodu. Tuš baterija je iz standardnog programa, a po izboru investitora. | Supply and installation of shower taps for hot and cold water. The shower tap is from the standard program and the investor's choice | kom/pcs |  | 2 | 0
49. |  | Nabavka, transport i ugradnja linijskog slivnika od polipropilena sa držačem rešetke napravljenim od ABS-a, bez bočnih ulaza i sa jednim horizontalnim ulazom DN 50 mm, minimalnom visinom ugradnje od 62 mm i maksimalnim protokom od 48 l/min. Baza slivnika bez mufa, sa vodenim čepom visine 25 mm, sa reducirom za linijske slivnike podesivim po visini i nožica za podešavanje visine i nagiba i rešetkom za dlake. Maska od prohroma sa sistemom 2 u 1, gde postoji mogućnost postavljanja keramike, mermera ili stakla u nju. Dužina kanala 65mm. Obračun po komadu komplet ugrađene i ispitane tuš kanalice. | Supply, transport and installation of the shower channel made of polypropylene with the grid holder made of ABS, without side entrances and with one horizontal inlet DN 50 mm, the minimum installation height of 62 mm and with a maximum flow of 48 l/min. The channel base is without muff, with water syphon 25 mm high, the reducer for linear drains adjustable in height, feet for height and grade adjustment and the hair grid. Mask made of chrome with a 2 in 1 system, where it is possible to place ceramics, marble or glass. Channel length 65mm. Calculation per piece, installed and tested shower channels | kom/pcs |  | 2 | 0
50. |  | Nabavka transport i montaža sudopera, sifon za sudoper sa odlivom i prelivom i priključkom za mašinu za suđe. Na sudoper ugraditi stojeću jednoručnu bateriju za toplu i hladnu vodu sa ugaonim ventilom i priključnim cevima. Obračun po kompletu. | Supply, transport and installation of the kitchen sink, with a siphon with drain and overflow and connection for the dishwasher. Install a standing single-lever tap for hot and cold water with an angle valve and connecting pipes on the sink. Calculation per set.
|  | jednodelna sudopera | one-piece sink | kom/pcs |  | 1 | 0
51. |  | Nabavka transport i montaža komplet zidnog pisaoara, domaće proizvodnje I klase. Pisoar preko gumenih podmetača pričvrstiti odgovarajućim tiplovima i mesinganim šrafovima. Postaviti hromirani propusni ventil i sifon. Pisoar naručiti po izboru investitora. Obračun po komplet pisoaru. | Supply, transport and installation of a set of the wall-mounted urinal, domestically produced, first class. Install the urinal over the rubber pads with suitable dowels and brass screws. Install the chrome-plated drain valve and siphon. Type of the urinal at the investor's choice. Calculation per set of urinals | kom/pcs |  | 16 | 0
VI. |  | SANITARNI PRIBORI | SANITARY EQUIPMENT AND ACCESSORIES |  |  | Ukupno/Total | 0
VII. |  | ATMOSFERSKA KANALIZACIJA | ATMOSPHERIC SEWAGE
52. |  | Nabavka, transport i ugradnja niskošumnih troslojnih kanalizacionih cevi i fitinga za unutrašnje instalacije, proizvedenih prema EN 1451 od polipropilena blok-kopolimera (PP-C) ojačanog sa mineralnim aditivima, sa spoljašnjim plavim i unutrašnjim belim slojem, i povećane absorbcije buke, a u svemu prema projektovanim prečnicima i datoj specifikaciji. Prateći sistem fitinga treba da bude ojačan u delu spojnice, sa dilatacionim distancerima i markerima za određivanje ugla rotacije fitinga i isporučen u zaštitnom PE pakovanju. Niskošumne cevi i fiting moraju da su testirane prema EN 14366 i DIN 4109 i da zadovolje zahteve minimalne zvučne izolacije od 12 dB(A), što dokazuje Fraunhofer-ov izveštaj o ispitivanju uz isporučene cevi. Radove izvesti u svemu prema tehničkim propisima za predviđenu vrstu cevi, odnosno u skladu sa zahtevima EN 12056 i SRPS ENV 13801, na način koji je predvideo proizvođač cevi i u skladu sa uputstvima Nadzornog organa. Obračun po metru dužnom. Ø110mm | Supply, transport and installation of low-noise three-layer sewer pipes and fittings for internal installations, manufactured according to EN 1451 from polypropylene block-copolymer (PP-C) reinforced with mineral additives, external blue and internal white layer, and increased noise absorption, according to designed diameters and given specification. The fitting system should be reinforced in the coupling part, with expansion spacers and markers for determining the angle of rotation of the fitting and delivered in a protective PE package. Low-noise pipes and fittings must be tested according to EN 14366 and DIN 4109 and fulfill minimum sound insulation requirements of 12 dB(A) by the Fraunhofer test report for the delivered pipes. The work must be carried out according to the technical regulations for this type of pipe, i.e. in accordance with the requirements of EN 12056 and SRPS ENV 13801, in the manner foreseen by the pipe manufacturer and in accordance with the instructions of the Supervisor Authority. Calculation per meter required. Ø110mm | m1 |  | 240 | 0
53. |  | Nabavka niskoprofilnog kanala za linijsko odvodnjavanja ACO DRAIN® Multiline V300E, prema SRPS EN 1433 i DIN 19580, sa sigurnosnim zaključavanjem rešetke bez zavrtnja tip Drainlock, napravljenog od ACO polimerbetona otpornog na dejstvo mraza i soli, sa integrisanim zaštitnim rubom od nerđajućeg čelika, sa preklopom i žljebom za jednostavno zaptivanje na mestu spoja dva kanala. Kanal je namenjen za opterećenja do klase D400. Elementi su dužine 100cm, nominalne širine 30cm, građevinske širine 35cm, građevinske visine 12cm. Priključak na kanalizaciju izvesti uz pomoć tela kanala sa vertikalnim priključkom sa integrisanom gumenom spojnicom za cev DN/OD100. | Supply of low-profile channel for linear drainage ACO DRAIN® Multiline V300E, according to SRPS EN 1433 and DIN 19580, with safety locking grid without screw top Drainlock, made of ACO polymer concrete resistant to the effects of frost and salt, with the integrated protective edge of folding steel, and groove for simple sealing at the connection of two channels. The channel is provided for traffic loads up to class D400. The elements are 100cm long, 30cm nominal width, 35cm construction width and 12cm construction height. Connect to the sewage system by the channel body with the vertical connection with the integrated rubber coupling for a pipe DN/OD100 | m1 |  | 16 | 0
54. |  | Nabavka rešetki za kanale za linijsko odvodnjavanje ACO Multiline V300 za klasu opterećenja A15 prema SRPS EN 1433 sa sigurnosnim zaključavanjem bez zavrtnja tip Drainlock i osiguranjem protiv podužnog pomeranja, napravljenih od nerđajućeg čelika,širina otvora 30x10mm, tip Mrežasta. Rešetka je širine 338 mm, dužine 50 cm, upojne površine 2032 cm²/m. Obračun po dužnom metru. | Supply of grids for linear drainage channels ACO Multiline V300 for load class A15 according to SRPS EN 1433 with safety locking without screws type Drainlock and insurance against the longitudinal movement, made of stainless steel, opening width 30x10mm, mesh type. The grid is 338 mm wide, 50 cm long, and has an absorbent surface of 2032 cm²/m. Calculation per meter. | m1 |  | 16 | 0
VII. |  | ATMOSFERSKA KANALIZACIJA | ATMOSPHERIC SEWAGE |  |  | Ukupno/ Total | 0
2.2. |  | REKAPITULACIJA - VODOVOD I KANALIZACIJA | SUMMARY- WATER SUPPLY AND SEWAGE INSTALLATION
I. |  | UREĐENJE TERENA - ZEMLJANI RADOVI | LANSCAPING - EARTHWORKS |  |  |  | 0
II. |  | INSTALATERSKI RADOVI I OPREMA | INSTALLATION WORKS AND EQUIPMENT |  |  |  | 0
III. |  | BETONSKI RADOVI ARMIRAČKI I RAZNI RADOVI | CONCRETE, REINFORCEMENT AND MISCELLANEOUS WORKS |  |  |  | 0
IV. |  | INSTALACIJE VODOVODA | WATER SUPPLY INSTALLATION |  |  |  | 0
V. |  | INSTALACIJE FEKALNE KANALIZACIJE | HOUSE SEWAGE INSTALLATION |  |  |  | 0
VI. |  | SANITARNI PRIBORI | SANITARY EQUIPMENT AND ACCESSORIES |  |  |  | 0
VII. |  | ATMOSFERSKA KANALIZACIJA | ATMOSPHERIC SEWAGE |  |  |  | 0
2.2. |  | UKUPNO VODOVOD I KANALIZACIJA | TOTAL WATER SUPPLY AND SEWAGE INSTALLATION |  |  |  | 0

## 2.3.saobraćaj-TRAFFIC
Program obrazovanja Crne Gore/ Education program of Montenegro
Predmjer - Izgradnja nove OŠ "Vladimir Nazor"/ Bill of Quantity - Construction of the new Elementary School "Vladimir Nazor" PROJEKAT SAOBRAĆAJA /TRAFFIC DESIGN
br/ No | predmet / subject | NASLOV | DESCRIPTION | mj.jedinica/ unit | pred.cijena u eurima/ unit price € | Količina / Quantity | Cijena u eurima (bez PDV-a) / Amount in € (excl VAT)
(a) | (b) | (c) |  | ( d ) | (e) | (f) | (g=e*f)
2.3. |  | PROJEKAT SAOBRAĆAJA | TRAFIC DESIGN
|  | PREDMJER I PREDRAČUN SAOBRAĆAJA | BILL OF QUANTITY OF TRAFFIC
I. |  | PRIPREMNI RADOVI | PREPARATORY WORKS
1. |  | Rušenje postojećih asfaltnih površina pretpostavljene debljine d=10 cm ( utovar i odvoz na gradsku deponiju obuhvaćen pozicijom skidanje površinskog sloja) | Demolition of existing asphalt surfaces with the assumed thickness of d=10 cm (loading and transport to the city landfill includes in the position cleaning of top-soil) | m2 |  | 94.19 | 0
2. |  | Rušenje postojećih betonskih površina pretpostavljene debljine d=10 cm ( utovar i odvoz na gradsku deponiju obuhvaćen pozicijom skidanje površinskog sloja) | Demolition of existing concrete surfaces with the assumed thickness of d=10 cm (loading and transport to the city landfill are included in the position cleaning of top-soil) | m2 |  | 20.94 | 0
3. |  | Uklanjanje dijela postojeće ograde sa utovarom i odvozom na gradsku deponiju | removal of part of the existing fence with loading and transport to the city landfill | m |  | 13.66 | 0
4. |  | Uklanjanje postojećeg drveća sa utovarom i odvozom na gradsku deponiju | removal of existing trees with loading and transport to the city landfill | kom/ pcs |  | 5 | 0
5. |  | Zasijecanje asfalta na vezi postojećeg asfaltnog puta i nove kolovozne konstrukcije | Asphalt cutting at the connection of the existing asphalt road and the new pavement structure | m |  | 26.2 | 0
6. |  | Struganje asfalta ( u širini od 30 cm i u debljini d =4 cm ) na vezi postojećeg asfaltnog puta i nove kolovozne konstrukcije sa utovarom i odvozom materijala na gradsku deponiju: | Asphalt milling (30 cm wide and d = 4 cm thick) on the connection of the existing asphalt road and the new road construction with loading and transport of the material to the city landfill | m2 |  | 7.83 | 0
I. |  | PRIPREMNI RADOVI | PREPARATORY WORKS |  |  | Ukupno/ Total | 0
II. |  | ZEMLJANI RADOVI | EARTH WORKS
7. |  | Skidanje površinskog sloja debljine d=40 cm , sa odvozom materijala na gradsku deponiju (ovom pozicijom je obuhvaćen i utovar i odvoz srušenih asfaltnih i betonskih površina): | Removal of the top-soil in the thickness of d=40 cm, with the transport of the material to the city landfill (this position also includes the loading and removal of demolished asphalt and concrete surfaces) | m3 |  | 733.01 | 0
8. |  | Mašinski iskop u širokom otkopu sa uklanjanjem I odvozom materijala na gradsku deponiju (ovom pozicijom je obuhvaćeno mašinsko uređenje posteljice do postizanja modula stišljivosti Ms≥40MPa) : u svim kategorijama tla i u gradskim uslovima | Mechanical-wide excavation with loading and transport of material to the city landfill (this position includes the mechanical preparation of the sub-soil until the compressibility module Ms≥40MPa is achieved) - in all soil categories and in city conditions | m3 |  | 1417.69 | 0
9. |  | Izrada nasipa od materijala V I VI kategorije iz pozajmišta (U cijenu uračunati nabavka, transport i ugradnja) | Performing embankments from materials of V and VI categories from the quarry (purchase, transport and performing are included in the price) | m3 |  | 25.01 | 0
10. |  | Zamjena materijala od drobljenog kamena u sloju debljine d=80 cm od materijala V i VI kategorije iz pozajmišta u skladu sa preporukama iz Geomehaničkog elaborata i izvrsiti zbijanje tog sloja do konsolidacije Ms≥50MPa (U cijenu uračunata nabavka, transport i ugradnja) | Replacement of existing material with crushed stone in the layer of d=80 cm from materials of V and VI categories from the quarry, in accordance with the recommendations from the Geotechnical study. Compaction of that layer to the consolidation of Ms≥50MPa (The price includes purchase, transport and performing of the layer). | m3 |  | 1466.7 | 0
11. |  | Obrada podtla | Preparation of sub-soil | m2 |  | 1858.46 | 0
12. |  | Izrada humuziranih bankina i bermi, d=10 cm (U cijenu uračunata nabavka, transport i ugradnja) | Preparation of shoulders and berms with the layer of humus d=10 cm (The price includes purchase, transport and performing of layer) | m2 |  | 5.54 | 0
13. |  | Ozeljenjavanje zelenih površina, d=10 cm (U cijenu uračunata nabavka, transport i ugradnja) | Filling of ''green areas'' with the layer of humus d=10 cm with grass sowing (The price includes purchase, transport and performing of the layer) | m2 |  | 91.94 | 0
II. |  | ZEMLJANI RADOVI | EARTH WORKS |  |  | Ukupno/Total | 0
III. |  | GORNJI SLOJ | UPPER LAYER (PAVEMENT STRUCTURE)
14. |  | Izrada donjeg nosećeg sloja ( tampona ) od drobljenog kamenog materijala 0/31 mm : * d=35 cm ispod kolovoza (Ms≥80 MPa), * d=20 cm ispod parking površina (Ms≥60 MPa) i (U cijenu uračunati nabavka, transport i ugradnja materijala ) | Performing of the lower bearing layer from crushed stone material 0/31 mm: * d=35 cm under the street (Ms≥80 MPa), * d=20 cm under the parking area (Ms≥60 MPa) ( the price includes purchase, transport and performing of the layer) | m3 |  | 476.86 | 0
15. |  | Nabavka, transport i izrada bitumeniziranog nosećeg sloja BNS-22, d = 6 cm (U poziciju uključeni nabavka, transport i ugradnja) | Purchase, transport and performing of bituminized bearing layer - asphalt concrete BNS-22, d = 6 cm (The position includes supply of component materials, transport and paving) | m2 |  | 737.62 | 0
16. |  | Nabavka, transport i izrada habajućeg sloja asfalt betona AB-11, d = 4 cm (U poziciju uključeni nabavka, transport i ugradnja) | Purchase, transport and performing of wearing course - asphalt concrete AB11, d = 4 cm (The position includes supply of component materials, transport and paving) | m2 |  | 745.45 | 0
17. |  | Nabavka, transport i ugradnja : | Purchase, transport and installation:
|  | ivičnjaka dimenzija 20/24 | - curbs dimension 20/24 | m1 |  | 287.53 | 0
|  | ivičnjaka dimenzija 18/24 | - curbs dimension 18/24 | m1 |  | 189.68 | 0
|  | "prelaznih" ivičnjaka | -"transition " curbs | m1 |  | 6.4 | 0
III. |  | GORNJI SLOJ | UPPER LAYER (PAVEMENT STRUCTURE) |  |  | Ukupno/Total | 0
IV. |  | OSTALI RADOVI | OTHER WORKS
18. |  | Izrada parking prostora od raster elemenata - beton trava debljine d=10 cm na sloju pijeska od d=2 cm (U poziciju uključeni nabavka, transport i ugradnja) | Paving of the parking spaces with raster elements (concrete - grass), the thickness d=10 cm, on the layer of sand of d=2 cm (The position includes purchase, transport and installation) | m2 |  | 724.43 | 0
19. |  | Izrada parking prostora od betonskih elemenata - behaton, na mjestima koja su označena za lica smanjene pokretljivosti, debljine d=8 cm na sloju pijeska od d=4 cm (U poziciju uključeni nabavka, transport i ugradnja) | Paving of the parking spaces with prefabricated concrete elements - behaton, on places marked for persons with disability, the thickness d=8 cm, on the layer of sand of d=4 cm (The position includes purchase, transport and installation) | m2 |  | 94.13 | 0
20. |  | Izrada rampi za lica smanjene pokretljivosti na pješačkim prelazima (U poziciju uključeni nabavka, transport i ugradnja) | Performing of ramps for people with disabilities at pedestrian crossings (The position includes purchase, transport and installation) | m2 | obračunato kroz poziciju izrade pješačkih staza oko objekta obuhvaćenih projektom arhitekture/ included in the position of the construction of pedestrian walkways around the building from the architecture design
21. |  | Izrada betonske trake, dimenzija 10cm x 15cm za razdvajanje parking mjesta (U poziciju uključeni nabavka, transport i ugradnja) | Performing the concrete strip, dimensions 10cm x 15cm, for dividing parking spaces (The position includes purchase, transport and all works) | m1 |  | 328.58 | 0
IV. |  | OSTALI RADOVI | OTHER WORKS |  |  | Ukupno/Total | 0
V. |  | NEPREDVIĐENI RADOVI 5% | UNFORESEEN WORKS 5% |  |  | Ukupno/Total | 0
2.3. |  | REKAPITULACIJA - PROJEKAT SAOBRAĆAJA | SUMMARY- TRAFFIC DESIGN
I. |  | PRIPREMNI RADOVI | PREPARATORY WORKS |  |  |  | 0
II. |  | ZEMLJANI RADOVI | EARTH WORKS |  |  |  | 0
III. |  | GORNJI SLOJ | UPPER LAYER (PAVEMENT STRUCTURE) |  |  |  | 0
IV. |  | OSTALI RADOVI | OTHER WORKS |  |  |  | 0
|  | UKUPNO I, II, III, IV | TOTAL I, II, III, IV |  |  |  | 0
V. |  | NEPREDVIĐENI RADOVI 5% | UNFORESEEN WORKS 5% |  |  |  | 0
2.3. |  | UKUPNO - PROJEKAT SAOBRAĆAJA | TOTAL - TRAFFIC DESIGN |  |  |  | 0

## 3.1.1.Jaka struja- HIGH VOLT
Program obrazovanja Crne Gore/ Education program of Montenegro
Predmjer - Izgradnja nove OŠ "Vladimir Nazor"/ Bill of Quantity - Construction of the new Elementary School "Vladimir Nazor" JAKA STRUJA/ HIGH VOLTAGE INSTALLATION
br/ No | predmet / subject | NASLOV | DESCRIPTION | mj.jedinica/ unit | pred.cijena u eurima/ unit price € | Količina / Quantity | Cijena u eurima (bez PDV-a) / Amount in € (excl VAT)
(a) | (b) | (c) |  | ( d ) | (e) | (f) | (g=e*f)
3.1.1. |  | JAKA STRUJA | HIGH VOLTAGE INSTALLATION
|  | PREDMJER I PREDRAČUN JAKE STRUJE | BILL OF QUANTITY HIGH VOLTAGE
I. |  | RAZVODNI ORMARI | DISTRIBUTION CABINETS
1. |  | Isporuka i ugradnja razvodnog ormara GRO, IP40 (fabričke ili radioničke izrade). Pod stavkom se podrazumijevaju i svi "sitni" elementi neophodni za ugradnju table, prekidača i ranžiranje kablova. U razvodne table se ugrađuju sledeći elementi: | Delivery and installation of distribution cabinet GRO, IP40 (factory or workshop production). The item also includes all "accessorize elements" elements necessary for installing the panel, switches and cable routing. The following elements are installed in the switchboards:
|  | NSX400N sa Micrologic 2.3, 3P | NSX400N with Micrologic 2.3, 3P | kom/pcs |  | 1
|  | Rastavljač sa osiguračima ISFT 250/160A, 1-0 3P | Disconnector with fuses ISFT 250160A, 1-0 3P | kom/pcs |  | 2
|  | Zaštitni uređaj diferencijalne struje Iid 25/0,03A, 4p | Differential current protective device Iid 25/0.03A, 4p | kom/pcs |  | 2
|  | Zaštitni uređaj diferencijalne struje Iid 40/0,03A, 4p | Differential current protective device Iid 40/0.03A, 4p | kom/pcs |  | 2
|  | Automatski prekidač iK60N-D/80A, 3p; 6kA | Automatic switch iK60N-D/80A, 3p; 6 kA | kom/pcs |  | 1
|  | Automatski prekidač iK60N-D/50A, 1p; 6kA | Automatic switch iK60N-D/50A, 1p; 6 kA | kom/pcs |  | 6
|  | Automatski prekidač iK60N-D/32A, 3p; 6kA | Automatic switch iK60N-D/32A, 3p; 6 kA | kom/pcs |  | 2
|  | Automatski prekidač iK60N-D/32A, 1p; 6kA | Automatic switch iK60N-D/32A, 1p; 6 kA | kom/pcs |  | 12
|  | Automatski prekidač iK60N-C/32A, 3p; 6kA | Automatic switch iK60N-C/32A, 3p; 6 kA | kom/pcs |  | 2
|  | Automatski prekidač iK60N-C/25A, 3p; 6kA | Automatic switch iK60N-C/25A, 3p; 6 kA | kom/pcs |  | 3
|  | Automatski prekidač iK60N-C/16A, 3p; 6kA | Automatic switch iK60N-C/16A, 3p; 6 kA | kom/pcs |  | 3
|  | Automatski prekidač iK60N-C/16A, 1p; 6kA | Automatic switch iK60N-C/16A, 1p; 6 kA | kom/pcs |  | 37
|  | Automatski prekidač iK60N-B/10A, 1p; 6kA | Automatic switch iK60N-B/10A, 1p; 6 kA | kom/pcs |  | 18
|  | Automatski prekidač iK60N-B/6A, 1p; 6kA | Automatic switch iK60N-B/6A, 1p; 6 kA | kom/pcs |  | 2
|  | Automatski prekidač iK60N-B/2A, 1p; 6kA | Automatic switch iK60N-B/2A, 1p; 6 kA | kom/pcs |  | 2
|  | 1-0, 16A za montažu na vratima | 1-0, 16A for installation on the door | kom/pcs |  | 2
|  | Rastavljač iSSW 20A, 1-0-2, 3P | Disconnector iSSW 20A, 1-0-2, 3P | kom/pcs |  | 1
|  | Vremenski relej(astronomski sat) | Time relay (astronomical clock) | kom/pcs |  | 1
|  | kontaktor 16A, 3NO,3P, 230Vac | Contactor 16A, 3NO, 3P, 230Vac | kom/pcs |  | 1
|  | kontaktor 16A, 2NO,2P, 230Vac | Contactor 16A, 2NO, 2P, 230Vac | kom/pcs |  | 1
|  | kontaktor 16A, 1NO,1P, 230Vac | Contactor 16A, 1NO, 1P, 230Vac | kom/pcs |  | 2
|  | Izborna sklopka 200A, 1-0-2, 4P | Selector switch 200A, 1-0-2, 4P | kom/pcs |  | 1
|  | signalna sijalica 230V, zelena, montaža na vratima | Signal bulb 230V, green, installation on the door | kom/pcs |  | 6
|  | Stavkom obuhvatiti sabirnice, redne stezaljke, POK kanali, plastične etikete, pertinaks, natpisne ploče, bakarne pletenice, uvodnice za kablove, jednopolna šema, džep za jednopolnu šemu i drugi potrebni sitni materijla neophodan za ugradnju ormana. Ukupno za materijal i rad: | The item includes busbars, row clamps, POK channels, plastic labels, pertinax, nameplates, copper braids, cable glands, single-pole scheme, pocket for the single-pole plan and other necessary small materials for the installation of the cabinet. Total for material and works | kom/pcs |  | 1 | 0
2. |  | Isporuka i ugradnja razvodnog ormara RO-PR, IP40 (fabričke ili radioničke izrade). Pod stavkom se podrazumijevaju i svi "sitni" elementi neophodni za ugradnju table, prekidača i ranžiranje kablova. | Delivery and installation of distribution box RO-PR, IP40 (factory or workshop production). The item also includes all "small" elements necessary for installing the panel, switches and cable routing. The following elements are installed in the switchboard:
|  | Rastavljač INS 40A, 1-0, 3P | Disconnector INS 40A, 1-0, 3P | kom/pcs |  | 1
|  | Rastavljač INS 63A, 1-0, 3P | Disconnector INS 63A, 1-0, 3P | kom/pcs |  | 1
|  | Zaštitni uređaj diferencijalne struje Iid 40/0,03A, 4p | Differential current protective device Iid 40/0.03A, 4p | kom/pcs |  | 1
|  | Zaštitni uređaj diferencijalne struje Iid 63/0,03A, 4p | Differential current protective device Iid 63/0.03A, 4p | kom/pcs |  | 1
|  | Automatski prekidač iK60N-C/16A, 1p; 6kA | Automatic switch iK60N-C/16A, 1p; 6 kA | kom/pcs |  | 61
|  | Automatski prekidač iK60N-B/10A, 1p; 6kA | Automatic switch iK60N-B/10A, 1p; 6 kA | kom/pcs |  | 26
|  | Automatski prekidač iK60N-B/6A, 1p; 6kA | Automatic switch iK60N-B/6A, 1p; 6 kA | kom/pcs |  | 3
|  | Automatski prekidač iK60N-B/2A, 1p; 6kA | Automatic switch iK60N-B/2A, 1p; 6 kA | kom/pcs |  | 2
|  | Rastavljač iSSW 20A, 1-0-2, 3P | Disconnector iSSW 20A, 1-0-2, 3P | kom/pcs |  | 5
|  | Vremenski relej(astronomski sat) | Time relay (astronomical clock) | kom/pcs |  | 1
|  | kontaktor 16A, 1NO, 1P, 230Vac | contactor 16A, 1NO, 1P, 230Vac | kom/pcs |  | 4
|  | kontaktor 16A, 3NO, 3P, 230Vac | contactor 16A, 3NO, 3P, 230Vac | kom/pcs |  | 1
|  | kontaktor 16A, 4NO, 4P, 230Vac | contactor 16A, 4NO, 4P, 230Vac | kom/pcs |  | 1
|  | 1-0, 16A za montažu na vratima | 1-0, 16A for door installing | kom/pcs |  | 5
|  | signalna sijalica 230V, zelena, montaža na vratima | Signal bulb 230V, green, installation on the door | kom/pcs |  | 6
|  | Stavkom obuhvatiti sabirnice, redne stezaljke, POK kanali, plastične etikete, pertinaks, natpisne ploče, bakarne pletenice, uvodnice za kablove, jednopolna šema, džep za jednopolnu šemu i drugi potrebni sitni materijla neophodan za ugradnju ormana. Ukupno za materijal i rad: | The item includes busbars, row clamps, POK channels, plastic labels, pertinax, nameplates, copper braids, cable glands, single-pole scheme, pocket for the single-pole scheme and other necessary small materials necessary for the installation of the cabinet. Total for material and works: | kom/pcs |  | 1 | 0
3. |  | Isporuka i ugradnja razvodnog ormara RO-1, IP40 (fabričke ili radioničke izrade). Pod stavkom se podrazumijevaju i svi "sitni" elementi neophodni za ugradnju table, prekidača i ranžiranje kablova. U razvodne table se ugrađuju sledeći elementi: | Delivery and installation of distribution box RO-1, IP40 (factory or workshop production). The item also includes all "small" elements necessary for installing the panel, switches and cable routing. The following elements are installed in the switchboards:
|  | Rastavljač INS 40A, 1-0, 3P | Disconnector INS 40A, 1-0, 3P | kom/pcs |  | 1
|  | Rastavljač INS 63A, 1-0, 3P | Disconnector INS 63A, 1-0, 3P | kom/pcs |  | 1
|  | Zaštitni uređaj diferencijalne struje Iid 40/0,03A, 4p | Differential current protective device Iid 40/0.03A, 4p | kom/pcs |  | 1
|  | Automatski prekidač iK60N-C/25A, 3p; 6kA | Automatic switch iK60N-C/25A, 3p; 6 kA | kom/pcs |  | 1
|  | Zaštitni uređaj diferencijalne struje Iid 63/0,03A, 4p | Differential current protective device Iid 63/0.03A, 4p | kom/pcs |  | 1
|  | Automatski prekidač iK60N-C/16A, 3p; 6kA | Automatic switch iK60N-C/16A, 3p; 6 kA | kom/pcs |  | 2
|  | Automatski prekidač iK60N-C/16A, 1p; 6kA | Automatic switch iK60N-C/16A, 1p; 6 kA | kom/pcs |  | 54
|  | Automatski prekidač iK60N-B/10A, 1p; 6kA | Automatic switch iK60N-B/10A, 1p; 6 kA | kom/pcs |  | 16
|  | Automatski prekidač iK60N-B/6A, 1p; 6kA | Automatic switch iK60N-B/6A, 1p; 6 kA | kom/pcs |  | 2
|  | Automatski prekidač iK60N-B/2A, 1p; 6kA | Automatic switch iK60N-B/2A, 1p; 6 kA | kom/pcs |  | 2
|  | Rastavljač iSSW 20A, 1-0-2, 3P | Disconnector iSSW 20A, 1-0-2, 3P | kom/pcs |  | 3
|  | kontaktor 16A, 1NO, 1P, 230Vac | contactor 16A, 1NO, 230Vac | kom/pcs |  | 2
|  | kontaktor 16A, 2NO, 2P, 230Vac | contactor 16A, 2NO, 230Vac | kom/pcs |  | 2
|  | signalna sijalica 230V, zelena, montaža na vratima | signal bulb 230V, green, installation on the door | kom/pcs |  | 6
|  | temperaturni kontroler za grijač slivnika ETO2-4550 | temperature controller for gully heater ETO2-4550 | kom/pcs |  | 1
|  | Stavkom obuhvatiti sabirnice, redne stezaljke, POK kanali, plastične etikete, pertinaks, natpisne ploče, bakarne pletenice, uvodnice za kablove, jednopolna šema, džep za jednopolnu šemu i drugi potrebni sitni materijla neophodan za ugradnju ormana. Ukupno za materijal i rad: | The item includes busbars, row clamps, POK channels, plastic labels, pertinax, nameplates, copper braids, cable glands, single-pole scheme, pocket for the single-pole scheme and other necessary small materials necessary for the installation of the cabinet. Total for material and works: | kom/pcs |  | 1 | 0
4. |  | Isporuka i ugradnja razvodnog ormara RO-2, IP40 (fabričke ili radioničke izrade). Pod stavkom se podrazumijevaju i svi "sitni" elementi neophodni za ugradnju table, prekidača i ranžiranje kablova. U razvodne table se ugrađuju sledeći elementi: | Delivery and installation of distribution box RO-2, IP40 (factory or workshop production). The item also includes all "small" elements necessary for installing the panel, switches and cable routing. The following elements are installed in the switchboards:
|  | Rastavljač INS 40A, 1-0, 3P | Disconnector INS 40A, 1-0, 3P | kom/pcs |  | 2
|  | Zaštitni uređaj diferencijalne struje Iid 40/0,03A, 4p | Differential current protective device Iid 40/0.03A, 4p | kom/pcs |  | 2
|  | Automatski prekidač iK60N-C/16A, 3p; 6kA | Automatic switch iK60N-C/16A, 3p; 6 kA | kom/pcs |  | 2
|  | Automatski prekidač iK60N-C/16A, 1p; 6kA | Automatic switch iK60N-C/16A, 1p; 6 kA | kom/pcs |  | 32
|  | Automatski prekidač iK60N-B/10A, 1p; 6kA | Automatic switch iK60N-B/10A, 1p; 6 kA | kom/pcs |  | 12
|  | Automatski prekidač iK60N-B/6A, 1p; 6kA | Automatic switch iK60N-B/6A, 1p; 6 kA | kom/pcs |  | 2
|  | Automatski prekidač iK60N-B/2A, 1p; 6kA | Automatic switch iK60N-B/2A, 1p; 6 kA | kom/pcs |  | 2
|  | Rastavljač iSSW 20A, 1-0-2, 3P | Disconnector iSSW 20A, 1-0-2, 3P | kom/pcs |  | 3
|  | kontaktor 16A, 1NO, 230Vac | contactor 16A, 1NO, 230Vac | kom/pcs |  | 2
|  | kontaktor 16A, 2NO, 230Vac | contactor 16A, 2NO, 230Vac | kom/pcs |  | 1
|  | kontaktor 20A, 2NO, 230Vac | contactor 20A, 2NO, 230Vac | kom/pcs |  | 1
|  | signalna sijalica 230V, zelena, montaža na vratima | Signal bulb 230V, green, installation on the door | kom/pcs |  | 6
|  | temperaturni kontroler za grijač slivnika ETO2-4550 | Temperature controller for gully heater ETO2-4550 | kom/pcs |  | 1
|  | Stavkom obuhvatiti sabirnice, redne stezaljke, POK kanali, plastične etikete, pertinaks, natpisne ploče, bakarne pletenice, uvodnice za kablove, jednopolna šema, džep za jednopolnu šemu i drugi potrebni sitni materijla neophodan za ugradnju ormana. Ukupno za materijal i rad: | The item includes busbars, row clamps, POK channels, plastic labels, pertinax, nameplates, copper braids, cable glands, single-pole scheme, pocket for the single-pole scheme and other necessary small materials necessary for the installation of the cabinet. Total for material and works | kom/pcs |  | 1 | 0
I. |  | RAZVODNI ORMARI | DISTRIBUTION CABINETS |  |  | Ukupno/Total | 0
II. |  | ELEKTRIČNA INSTALACIJA OPŠTE POTROŠNJE | ELECTRICAL INSTALLATION OF GENERAL CONSUMPTION
5. |  | Nabavka, isporuka i izvođenje provodnika tipa. Stavkom obuhvatiti sav montažni materijal koje je neophodan za ugradnju provodnika kao i povezivanje provodnika na oba kraja. Takodje stavkom je obuhvaćeno štemanje betonskih površina u odnosu 25% od ukupne dužine svih kablova. Ukupno za materijal i rad: | Procurement, delivery and execution of mentioned type conductors. The item includes all material that is necessary for the installation of the conductor as well as the connection of the conductor at both ends. The item also cut channels for cables in the concrete walls, about 25% of the total length of all cables. Total for material and works:
|  | N2XH-J 3x2,5mm² | N2XH-J 3x2,5mm² | m1 |  | 13000 | 0
|  | N2XH-J 5x2,5mm² | N2XH-J 5x2,5mm² | m1 |  | 200 | 0
|  | N2XH-J 5x6mm² | N2XH-J 5x6mm² | m1 |  | 40 | 0
|  | N2XH-J 5x16mm² | N2XH-J 5x16mm² | m1 |  | 200 | 0
|  | N2XH-J 5x10mm² | N2XH-J 5x10mm² | m1 |  | 320 | 0
|  | N2XH 4x25+1x16mm² | N2XH 4x25+1x16mm² | m1 |  | 50 | 0
|  | NHXH FE180E90 4x120mm² | NHXH FE180E90 4x120mm² | m1 |  | 15 | 0
|  | NHXH FE180E90 5x2,5mm² | NHXH FE180E90 5x2,5mm² | m1 |  | 50 | 0
|  | NHXH FE180E90 5x10mm² | NHXH FE180E90 5x10mm² | m1 |  | 100 | 0
|  | LiHCH 3x1,5mm² | LiHCH 3x1,5mm² | m1 |  | 160 | 0
|  | PP00-y 3x2,5mm² | PP00-y 3x2,5mm² | m1 |  | 250 | 0
|  | N2XH-J 3x1,5mm² | N2XH-J 3x1,5mm² | m1 |  | 15600 | 0
6. |  | Nabavka, isporuka i izvođenje montažnog materijala neophodnog za ugradnju i polaganje kablova( korugovane savitljive cijevi, obujmice itd.). Ukupno za materijal i rad: | Procurement, delivery and execution of assembly material necessary for installing cables (flexible corrugated pipes, clamps, etc.). Total for material and works: | m1 |  | 1 | 0
7. |  | Nabavka, isporuka i polaganje sapa instalacionih PVC cijevi 16mm/13.7mm. Stavkom obuhvatiti sav montažni materijal neophodan za njihovu ugradnju (obujmice, šarafi, podloške, lukovi, spojnice...) Ukupno za materijal i rad: | Procurement, delivery and installation of PVC installation pipes 16mm/13.7mm. The item includes all assembly materials necessary for their installation (clamps, screws, washers, bows, connectors...) Total for material and work: | m1 |  | 250 | 0
8. |  | Nabavka, isporuka vatrootporne mase za premazivanje provodnika na mjestu prodora kablova u objekat, kao i na mjestima prelaska iz jedne požarne zone u drugu. Ukupno za materijal i rad: | Procurement and delivery of fire-resistant compound for coating conductors at the point of penetration of cables into the building. Total for material and works: | kg |  | 10 | 0
II. |  | ELEKTRIČNA INSTALACIJA OPŠTE POTROŠNJE | ELECTRICAL INSTALLATION OF GENERAL CONSUMPTION |  |  | Ukupno/Total | 0
III. |  | ELEKTRIČNA INSTALACIJA OSVJETLJENJA | ELECTRICAL LIGHTING INSTALLATION
9. |  | (S1) Nabavka,isporuka i ugradnja nadgradne LED svjetiljke, ukupne ulazne snage 41.7W, izlazni svjetlosni fluks svjetiljke 5180lm, temperatura boje svijetla 4000K, efikasnost svjetiljke 124lm/W, sa Wide Beam optikom, karakteristike izvora svijetla MacAdam 3, 50.000 radnih sati prije opadanja svjetlosnog fluksa na 80% inicijalne vrijednosti pri 25°C, el. predspojni uredjaj integrisan unutar svjetiljke, laka montaza sa patentiranim snap-on mehanizmom, predvidjena za montazu na plafonima i zidovima, rad na ambijentalnoj temperaturi od -20°C do +33°C, izradjena od polikarbonata, sive boje, stepena zastite IP66, mehanicke zastite IK08, posjeduje CE, RCM i ENEC sertifikat, dimenzija 1600x92x90 mm, mase 1.85kg, slična tipu AQFPRO S LED5200-840 PC WB HF proizvođača Thorn ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Svjetiljka se isporucuje u kompletu sa izvorom svijetla i svom potrebnom opremom za rad. Ukupno za materijal i rad: | (S1) Procurement, delivery and installation of a surface LED lamp, total input power 41.7W, lamp output luminous flux 5180lm, light colour temperature 4000K, lamp efficiency 124lm/W, with Wide Beam optics, light source characteristics MacAdam 3, 50,000 working hours before decrease of the luminous flux to 80% of the initial value at 25°C, pre switching device integrated inside the lamp, easy installation with patented snap-on mechanism, intended for installation on ceilings and walls, operation at ambient temperature from -20°C to +33°C, made of polycarbonate, grey colour, degree of protection IP66, mechanical protection IK08, has CE, RCM and ENEC certificate, dimensions 1600x92x90 mm, weight 1.85 kg, similar to type AQFPRO S LED5200-840 PC WB HF manufactured by Thorn or the equivalent of another manufacturer with the same or better characteristic. The lamp is delivered with a light source and all the necessary equipment for work. Total for material and works: | kom/pcs |  | 29 | 0
10. |  | (S2) Nabavka isporuka i ugradnja ugradne plafonske LED svjetiljke, ukupne ulazne snage 15.5W, izlazni svjetlosni fluks svjetiljke 2048lm, temperatura boje svijetla 4000K, efikasnost svjetiljke 132lm/W, karakteristike izvora svijetla MacAdam 3, UGR<25, 50.000 radnih sati prije opadanja svjetlosnog fluksa na 80% inicijalne vrijednosti pri 25°C, el. predspojni uredjaj integrisan unutar svjetiljke, IEC EN 60598-1 RG 1, izrađena od aluminijuma, bijele boje, svjetiljka posjeduje CE/UKCA i ENEC sertifikat, stepena zastite sa donje strane IP44 sa gornje strane IP20, mehanicke zastite IK06, dimenzija Ø195x100mm, mase 0.56 kg, slična tipu CETUS3 M 2000-840 HF RWH proizvođača Thorn ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Svjetiljka se isporucuje u kompletu sa izvorom svijetla i svom potrebnom opremom za rad. Ukupno za materijal i rad: | (S2) Procurement, delivery and installation of a built-in LED ceiling lamp, total input power 15.5W, lamp output luminous flux 2048lm, light colour temperature 4000K, lamp efficiency 132lm/W, light source characteristics MacAdam 3, UGR<25, 50,000 working hours before deterioration luminous flux to 80% of the initial value at 25°C, pre switching device integrated inside the lamp, IEC EN 60598-1 RG 1, made of aluminium, white colour, the light has CE/UKCA and ENEC certificate, degree of protection on the lower side IP44 on the upper side IP20, mechanical protection IK06, dimensions Ø195x100mm, mass 0.56 kg, similar to the type CETUS3 M 2000-840 HF RWH manufactured by Thorn. The lamp is delivered with a light source and all the necessary equipment for work. Total for material and works: | kom/pcs |  | 152 | 0
11. |  | (S3) Nabavka isporuka i ugradnja ugradne plafonske LED svjetiljke, ukupne ulazne snage 25.4W, izlazni svjetlosni fluks svjetiljke 3463lm, temperatura boje svijetla 4000K, efikasnost svjetiljke 136lm/W, karakteristike izvora svijetla MacAdam 3, UGR<25, CRI>80, 50.000 radnih sati prije opadanja svjetlosnog fluksa na 80% inicijalne vrijednosti pri 25°C, el. predspojni uredjaj integrisan unutar svjetiljke, IEC EN 60598-1 RG 1, izrađena od aluminijuma, bijele boje, svjetiljka posjeduje CE/UKCA i ENEC sertifikat, stepena zastite sa donje strane IP44 sa gornje strane IP20, mehanicke zastite IK06, dimenzija Ø248x100mm, mase 0.7 kg, slična tipu CETUS3 L 3000-840 HF RWH proizvođača Thorn ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Svjetiljka se isporucuje u kompletu sa izvorom svijetla i svom potrebnom opremom za rad. Ukupno za materijal i rad: | (S3) Procurement, delivery and installation of a built-in ceiling LED lamp, total input power 25.4W, luminous output flux of the lamp 3463lm, light colour temperature 4000K, lamp efficiency 136lm/W, light source characteristics MacAdam 3, UGR<25, CRI>80, 50,000 working hours before the luminous flux drops to 80% of the initial value at 25°C, pre switching device integrated inside the lamp, IEC EN 60598-1 RG 1, made of aluminium, white colour, the light has CE/UKCA and ENEC certificate, degree of protection on the lower side IP44 on the upper side IP20, mechanical protection IK06, dimensions Ø248x100mm, mass 0.7 kg, similar to the type CETUS3 L 3000-840 HF RWH manufactured by Thorn. The lamp is delivered with a light source and all the necessary equipment for work. Total for material and works: | kom/pcs |  | 104 | 0
12. |  | (S4) Nabavka isporuka i ugradnja ugradne plafonske LED svjetiljke, ukupne ulazne snage 17.2W, izlazni svjetlosni fluks svjetiljke 2090lm, temperatura boje svijetla 4000K, efikasnost svjetiljke 122lm/W, karakteristike izvora svijetla MacAdam 3, UGR<22, CRI>80, 50.000 radnih sati prije opadanja svjetlosnog fluksa na 80% inicijalne vrijednosti pri 25°C, el. predspojni uredjaj integrisan unutar svjetiljke, izrađena od aluminijuma, bijele boje, svjetiljka posjeduje CE/UKCA, RCM, CB, EPD i ENEC sertifikat, stepena zastite sa donje strane IP54 sa gornje strane IP20, mehanicke zastite IK03, dimenzija Ø220x94mm, mase 0.91 kg, slična tipu CHAL 200 LED2000-840 HF RSB proizvođača Thorn ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Svjetiljka se isporucuje u kompletu sa izvorom svijetla i svom potrebnom opremom za rad. Ukupno za materijal i rad: | (S4) Procurement, delivery and installation of a built-in ceiling LED lamp, total input power 17.2W, luminous output flux of the lamp 2090lm, light colour temperature 4000K, lamp efficiency 122lm/W, light source characteristics MacAdam 3, UGR<22, CRI>80, 50,000 working hours before the luminous flux drops to 80% of the initial value at 25°C, pre switching device integrated inside the lamp, made of aluminium, white colour, the light has CE/UKCA, RCM, CB, EPD and ENEC certificate, degree of protection on the lower side IP54 on the upper side IP20, mechanical protection IK03, dimensions Ø220x94mm, weight 0.91 kg, similar to the type CHAL 200 LED2000-840 HF RSB manufactured by Thorn. The lamp is delivered with a light source and all the necessary equipment for work. Total for material and works: | kom/pcs |  | 12 | 0
13. |  | (S5) Nabavka isporuka i ugradnja ugradne plafonske LED svjetiljke, ukupne ulazne snage 19W, izlazni svjetlosni fluks svjetiljke 2419lm, StableWhite svjetiljka, temperatura boje svijetla 4000K, efikasnost svjetiljke 127lm/W, karakteristike izvora svijetla MacAdam 3, UGR<19, CRI>80, 50.000 radnih sati prije opadanja svjetlosnog fluksa na 85% inicijalne vrijednosti pri 25°C, el. predspojni uredjaj integrisan unutar svjetiljke, izrađena od aluminijuma, bijele boje, otporna na UV zracenje, svjetiljka posjeduje CE/UKCA, RCM, CB, EPD i ENEC sertifikat, stepena zastite sa donje strane IP44 sa gornje strane IP20, mehanicke zastite IK04, dimenzija Ø218x119mm, mase 0.91 kg, slična tipu PANOS EVO R200H 19W LED840 SWI FAL WH proizvođača Zumtobel ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Svjetiljka se isporucuje u kompletu sa izvorom svijetla i svom potrebnom opremom za rad. Ukupno za materijal i rad: | (S5) Procurement, delivery and installation of a built-in LED ceiling lamp, total input power 19W, lamp output luminous flux 2419lm, StableWhite lamp, light colour temperature 4000K, lamp efficiency 127lm/W, light source characteristics MacAdam 3, UGR<19, CRI>80, 50,000 operating hours before the luminous flux decreases to 85% of the initial value at 25°C, pre switching device integrated inside the lamp, made of aluminium, white colour, resistant to UV radiation, the light has CE/UKCA, RCM, CB, EPD and ENEC certificate, degree of protection on the lower side IP44 on the upper side IP20, mechanical protection IK04, size Ø218x119mm, weight 0.91 kg, similar to the type PANOS EVO R200H 19W LED840 SWI FAL WH manufactured by Zumtobel or the equivalent of another manufacturer with the same or better characteristic. The lamp is delivered with a light source and all the necessary equipment for work. Total for material and works: | kom/pcs |  | 24 | 0
14. |  | (S6) Nabavka isporuka i ugradnja ugradne plafonske LED svjetiljke, ukupne ulazne snage 25.7W, izlazni svjetlosni fluks svjetiljke 3750lm, temperatura boje svijetla 4000K, efikasnost svjetiljke 146lm/W, optika u vidu saca koja pruza koeficijent blijestanja UGR<16 i L65<1000cd/m2 po EN 12464:2011, karakteristike izvora svijetla MacAdam 3, 100.000 radnih sati prije opadanja svjetlosnog fluksa na 95% inicijalne vrijednosti pri 25°C, el. predspojni uredjaj integrisan unutar svjetiljke, kuciste svjetiljke izradjeno od celicnog lima sa emajliranim zavrsetkom u bijeloj boji, stepena zastite IP40, dimenzija 598x598x74mm, tezine 6.62kg, svjetiljka posjeduje CE/UKCA, EPD i ENEC sertifikat, slična tipu MIRL NIV LED3800-840M600Q EVG proizvođača Zumtobel ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Svjetiljka se isporucuje u kompletu sa izvorom svijetla, priborom za montazu i svom potrebnom opremom za rad. Ukupno za materijal i rad: | (S6) Procurement, delivery and installation of a built-in ceiling LED lamp, total input power 25.7W, luminous output flux of the lamp 3750lm, light colour temperature 4000K, lamp efficiency 146lm/W, optics in the form of a glass that provides a glare coefficient UGR<16 and L65<1000cd /m2 according to EN 12464:2011, characteristics of the light source MacAdam 3, 100,000 working hours before the luminous flux decreases to 95% of the initial value at 25°C, pre switching device integrated inside the lamp, lamp housing made of steel sheet with white enamel finish, degree of protection IP40, dimensions 598x598x74mm, weight 6.62kg, the lamp has CE/UKCA, EPD and ENEC certificate, similar to type MIRL NIV LED3800-840M600Q EVG manufacturer Zumtobel. The lamp is delivered with a light source, mounting accessories and all necessary work equipment. Total for material and works: | kom/pcs |  | 361 | 0
15. |  | Nabavka, isporuka i ugradnja pribora za ugradnu montazu svjetiljke MIREL. Ukupno za materijal i rad: | Procurement, delivery and installation of accessories for the built-in installation of the MIREL lamp. Total for material and works: | kom/pcs |  | 361 | 0
16. |  | (S7) Nabavka isporuka i ugradnja ugradne plafonske LED visilice, ukupne ulazne snage 18.6W, izlazni svjetlosni fluks svjetiljke 1690lm, temperatura boje svijetla 4000K, efikasnost svjetiljke 91lm/W, karakteristike izvora svijetla MacAdam 3, UGR<19, CRI>80, 50.000 radnih sati prije opadanja svjetlosnog fluksa na 90% inicijalne vrijednosti pri 25°C, el. predspojni uredjaj integrisan unutar svjetiljke, izrađena od aluminijuma, bijele boje, svjetiljka posjeduje CE/UKCA i EAC sertifikat, stepena zastite IP20, mehanicke zastite IK05, dimenzija 1000x72x88mm, mase 2.1 kg, slična tipu EQL C L1000 LRO WH proizvođača Thorn ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Svjetiljka se isporucuje u kompletu sa izvorom svijetla i svom potrebnom opremom za rad. Ukupno za materijal i rad: | (S7) Procurement, delivery and installation of a built-in ceiling LED pendant, total input power 18.6W, lamp output luminous flux 1690lm, light colour temperature 4000K, lamp efficiency 91lm/W, light source characteristics MacAdam 3, UGR<19, CRI>80, 50,000 working hours before the luminous flux drops to 90% of the initial value at 25°C, pre switching device integrated inside the lamp, made of aluminium, white colour, the light has CE/UKCA and EAC certificate, degree of protection IP20, mechanical protection IK05, dimensions 1000x72x88mm, weight 2.1 kg, similar to type EQL C L1000 LRO WH manufactured by Thorn or the equivalent of another manufacturer with the same or better characteristic. The lamp is delivered with a light source and all the necessary equipment for work. Total for material and works: | kom/pcs |  | 9 | 0
17. |  | Nabavka, isporuka i ugradnja ovjesnog pribora za montazu svjetiljke EQUALINE. Ukupno za materijal i rad: | Procurement, delivery and installation of suspension accessories for mounting the EQUALINE lamp. Total for material and works: | kom/pcs |  | 9 | 0
18. |  | (S8) Nabavka,isporuka i ugradnja ugradne LED svjetiljke, ukupne ulazne snage 9.4W, izlazni svjetlosni fluks svjetiljke 950lm, temperatura boje svijetla 4000K, efikasnost svjetiljke 101lm/W, karakteristike izvora svijetla MacAdam 3, 50.000 radnih sati prije opadanja svjetlosnog fluksa na 70% inicijalne vrijednosti pri 25°C, el.eksterni predspojni uredjaj, izradjena od aluminijuma, bijele boje, klasa elektricne izolacije II, stepena zastite IP20/65 sa donje strane, mehanicke zastite IK04, posjeduje CE/UKCA i RCM sertifikat, dimenzija Ø87 x 77 mm, mase 0.4 kg, slična tipu CHAL 74 LED900-840 WFL IP65 WHM proizvođača Thorn ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Svjetiljka se isporucuje u kompletu sa izvorom svijetla i svom potrebnom opremom za rad. Ukupno za materijal i rad: | (S8) Procurement, delivery and installation of a built-in LED lamp, total input power 9.4W, lamp output luminous flux 950lm, light colour temperature 4000K, lamp efficiency 101lm/W, light source characteristics MacAdam 3, 50,000 working hours before the luminous flux drops to 70 % of initial value at 25°C, external electrical pre switching device, made of aluminium, white colour, electrical insulation class II, degree of protection IP20/65 on the bottom side, mechanical protection IK04, has CE/UKCA and RCM certificate, size Ø87 x 77 mm, mass 0.4 kg, similar to type CHAL 74 LED900-840 WFL IP65 WHM manufactured by Thorn. The lamp is delivered with a light source and all the necessary equipment for work. Total for material and works: | kom/pcs |  | 4 | 0
19. |  | (S9) Nabavka,isporuka i ugradnja nadgradne LED svjetiljke, ukupne ulazne snage 16.3W, izlazni svjetlosni fluks svjetiljke 1950lm, temperatura boje svijetla 4000K, efikasnost svjetiljke 120lm/W, karakteristike izvora svijetla MacAdam 3, 50.000 radnih sati prije opadanja svjetlosnog fluksa na 80% inicijalne vrijednosti pri 25°C, el. predspojni uredjaj integrisan unutar svjetiljke, izradjena od polikarbonata, sive boje, stepena zastite IP65, mehanicke zastite IK10, u skladu sa specifikacijama Međunarodnog standarda za hranu (HACCP standard), posjeduje CE/UKCA, CB, FOOD, EPD i ENEC sertifikat, dimenzija Ø307 x 58 mm, mase 0.98 kg, slična tipu KAT RD 2000-840 HF proizvođača Thorn ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Svjetiljka se isporucuje u kompletu sa izvorom svijetla i svom potrebnom opremom za rad. Ukupno za materijal i rad: | (S9) Procurement, delivery and installation of an overhead LED lamp, total input power 16.3W, luminous output flux of the lamp 1950lm, light colour temperature 4000K, lamp efficiency 120lm/W, characteristics of the light source MacAdam 3, 50,000 working hours before the luminous flux drops to 80 % of initial value at 25°C, pre switching device integrated inside the lamp, made of polycarbonate, grey colour, degree of protection IP65, mechanical protection IK10, in accordance with the specifications of the International Food Standard (HACCP standard), has CE/UKCA, CB, FOOD, EPD and ENEC certificate, size Ø307 x 58 mm, weight 0.98 kg, similar to the KAT RD 2000-840 HF manufactured by Thorn. The lamp is delivered with a light source and all the necessary equipment for work. Total for material and works: | kom/pcs |  | 6 | 0
20. |  | (S10) Nabavka isporuka i ugradnja ugradnee plafonske LED svjetiljke za skolske table, ukupne ulazne snage 37.7 W, izlazni svjetlosni fluks svjetiljke 4400lm, temperatura boje svijetla 4000K, efikasnost svjetiljke 117lm/W, karakteristike izvora svijetla MacAdam 3, 50.000 radnih sati prije opadanja svjetlosnog fluksa na 95% inicijalne vrijednosti pri 25°C, el. predspojni uredjaj integrisan unutar svjetiljke,izrađena od čeličnog lima, bijele boje, stepena zastite IP20, dimenzija 1198x114x85mm, mase 3.84 kg, slična tipu FEW LED4400-840 M600L12 LDE proizvođača Zumtobel ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Svjetiljka se isporucuje u kompletu sa izvorom svijetla i svom potrebnom opremom za rad. Ukupno za materijal i rad: | (S10) Procurement, delivery and installation of a built-in LED ceiling lamp for school blackboards, total input power 37.7 W, lamp output luminous flux 4400lm, light colour temperature 4000K, lamp efficiency 117lm/W, light source characteristics MacAdam 3, 50,000 working hours before light decay flux to 95% of the initial value at 25°C, pre switching device integrated inside the lamp, made of sheet steel, white colour, degree of protection IP20, dimensions 1198x114x85mm, weight 3.84 kg, similar to type FEW LED4400-840 M600L12 LDE manufactured by Zumtobel. The lamp is delivered with a light source and all the necessary equipment for work. Total for material and works: | kom/pcs |  | 58 | 0
21. |  | (S11) Nabavka isporuka i ugradnja nadgradne LED svjtetiljke, ukupne ulazne snage 16.3W, izlazni svjetlosni fluks svjetiljke 1950lm, temperatura boje svijetla 3000K, efikasnost svjetiljke 120lm/W, karakteristike izvora svijetla MacAdam 3, 50.000 radnih sati prije opadanja svjetlosnog fluksa na 80% inicijalne vrijednosti pri 25°C, el. predspojni uredjaj integrisan unutar svjetiljke, izradjena od polikarbonata, sive boje, stepena zastite IP65, mehanicke zastite IK10, u skladu sa specifikacijama Međunarodnog standarda za hranu (HACCP standard), posjeduje CE/UKCA, CB, FOOD, EPD i ENEC sertifikat, dimenzija Ø307 x 58 mm, mase 0.98 kg, slična tipu KAT RD 2000-830 HF proizvođača Thorn ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Svjetiljka se isporucuje u kompletu sa izvorom svijetla i svom potrebnom opremom za rad. Ukupno za materijal i rad: | (S11) Procurement, delivery and installation of a surface LED light, total input power 16.3W, luminous output flux of the lamp 1950lm, light colour temperature 3000K, lamp efficiency 120lm/W, characteristics of the light source MacAdam 3, 50,000 working hours before the luminous flux drops to 80% initial values at 25°C, pre switching device integrated inside the lamp, made of polycarbonate, grey colour, degree of protection IP65, mechanical protection IK10, in accordance with the specifications of the International Food Standard (HACCP standard), has CE/UKCA, CB, FOOD, EPD and ENEC certificate, size Ø307 x 58 mm, mass 0.98 kg, similar to type KAT RD 2000-830 HF manufactured by Thorn. The lamp is delivered with a light source and all the necessary equipment for work. Total for material and works: | kom/pcs |  | 14 | 0
22. |  | (P1) Nabavka, isporuka i ugradnja nadgradne anti panik svjetiljke, ukupne ulazne snage 3.4W, izlazni svjetlosni fluks svjetiljke 84lm, boja svijetla 6200K, 50.000 radnih sati prije opadanja svjetlosnog fluksa na 85% inicijalne vrijednosti pri 25°C, svjetiljka izdradjena od polikarbonata, bijele boje, svjetiljka je autonomije 3h, zaštite IP65, mehaničke zaštite IK07, mogućnost samotestiranja, posjeduje CE/UKCA sertifikat, dimenzija 280 x 130 x 71 mm, tezine 0.68kg, slicna tipu VOYAGER SOLID MS E3-S WH proizvodjaca Thorn ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Ukupno za materijal i rad: | (P1) Procurement, delivery and installation of an anti-panic lamp, installation in front of the wall or on ceiling total input power 3.4W, luminous output flux of the lamp 84lm, light colour 6200K, 50,000 working hours before the luminous flux decreases to 85% of the initial value at 25°C, lamp made of polycarbonate, white colour, the light has an autonomy of 3h, protection IP65, mechanical protection IK07, the possibility of self-testing, has a CE/UKCA certificate, dimensions 280 x 130 x 71 mm, weight 0.68 kg, similar to the type VOYAGER SOLID MS E3-S WH manufactured by Thorn or the equivalent of another manufacturer with the same or better characteristic. Total for material and works: | kom/pcs |  | 28 | 0
23. |  | Nabavka, isporuka i ugranja piktograma tipa VOYAGER SOLID 115 MSC SM-S ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Ukupno za materijal i rad: | Procurement, delivery and installation of VOYAGER SOLID 115 MSC SM-S pictograms. Total for material and works: | kom/pcs |  | 28 | 0
24. |  | (P2) Nabavka, isporuka i ugradnja LED piktograma, autonomije 1,2,3 ili 8h, u pripravnom ili trajnom spoju, kuciste svjetiljke izrađeno od polikarbonata ( RAL9016 ), ocekivani zivotni vijek je 50.000 radnih sati, uniformisan osvjetiljaj piktograma >500cd/m2, svjetiljka se lako montira, u kompletu sa piktogramima po ISO 7010 standardu, maksimalna vidljiva daljina 23m, svjeitljku nije potrebno odrzavati zahvaljujuci LED tehnologiji, zastite IP40, mehanicke zastite IK03, mogucnost rada na ambijentalnoj temperaturi od 5°C do 40°C, dimenzija 330x45x190mm, tezine 0.8kg, slicna tipu VOYAGER BLADE 2 115 MS E1/2/3/8 WH, proizvodjaca THORN Lighting, zemlja Engleska ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Ukupno za materijal i rad: | (P2) Procurement, delivery and installation of LED pictograms, autonomy 1,2,3 or 8h, in standby or permanent connection, lamp housing made of polycarbonate (RAL9016), expected lifetime is 50,000 working hours, uniform illumination of the pictogram >500cd/m2, the lamp is easy to mount, complete with pictograms according to the ISO 7010 standard, maximum visible distance 23m, the light does not need to be maintained because to LED technology, protection IP40, mechanical protection IK03, the possibility of working at ambient temperatures from 5°C to 40°C, dimensions 330x45x190mm, weight 0.8kg, similar to VOYAGER BLADE 2 115 MS E1/2/3/8 WH, manufactured by THORN Lighting, country of England or the equivalent of another manufacturer with the same or better characteristic. Total for material and works | kom/pcs |  | 90 | 0
25. |  | (P3) Nabavka, isporuka i ugradnja nadgradne LED svetiljke za osvetljenje antipanik zona sa min. 0.5 lux u skladu sa EN 1838; neutralno bijela 4000K; ukupne ulazne snage 9.3W, izlazni svjetlosni fluks svjetiljke 385lm, efikasnost svjetiljke 41lm/W, karakteristike izvora svijetla MacAdam 5, sočivo od polikarbonata CRI>70, 100.000 radnih sati prije opadanja svjetlosnog fluksa na 95% inicijalne vrijednosti pri 25°C, Napravljena od livenog aluminijuma; boja kućišta bijela (RAL9016); Nosač zupčanika od pocinkovanog lima; Svetiljka sa lokalnim napajanjem iz autonomije 3 sata, sa automatskim testom (automatsko testiranje) preko svjetiljke, opcionalno centralno nadgledanje preko DALI, prikaz stanja svetiljke putem LED stanja; NFC interfejs za adresiranje, konfiguraciju i održavanje putem PROset olovke ili aplikacije PROset; obraćanje takođe moguće vizuelno ili putem EZ-obraćanja; napajanje: 220-240 V AC (+/- 10%), 50-60 Hz; SC1; Utični terminali za prolazno ožičenje do 2,5 mm²; Udarna čvrstoća: IK04; svjetiljka posjeduje CE/UKCA i ENEC sertifikat, dimenzije: 200x145x64 mm; težina: 1,1 kg; slična tipu RESCLITE PRO M MSC ANT HP E3D WH IP65, proizvođača Zumtobel ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Svjetiljka se isporucuje u kompletu sa izvorom svjetla, potrebnom opremom za rad. Ukupno za materijal i rad: | (P3) Procurement, delivery and installation of an overhead LED lamp for anti-panic zone lighting with min. 0.5 lux in accordance with EN 1838; neutral white 4000K; total input power 9.3W, lamp output luminous flux 385lm, lamp efficiency 41lm/W, light source characteristics MacAdam 5, polycarbonate lens CRI>70, 100,000 working hours before the luminous flux declines to 95% of the initial value at 25°C, Made of cast aluminum; housing color white (RAL9016); Gear carrier made of galvanized sheet metal; Luminaire with local power supply from autonomy of 3 hours, with automatic test by the lamp, optional central monitoring by DALI, display of the status of the luminaire by LED status; NFC interface for addressing, configuration and maintenance via PROset pen or PROset application; addressing is possible visually or via EZ-address; power supply: 220-240 V AC (+/- 10%), 50-60 Hz; SC1; Plug-in terminals for through wiring up to 2.5 mm²; Impact strength: IK04; the lamp has a CE/UKCA and ENEC certificate, dimensions: 200x145x64 mm; weight: 1.1 kg; similar to the type RESCLITE PRO M MSC ANT HP E3D WH IP65, manufactured by Zumtobel or the equivalent of another manufacturer with the same or better characteristic. The lamp is delivered with a light source and necessary equipment for work. Total for material and works: | kom/pcs |  | 10 | 0
26. |  | (P4) Nabavka, isporuka i ugradnja ugradne LED svetiljke za osvetljenje antipanik zona sa min. 0.5 lux u skladu sa EN 1838; neutralno bijela 4000K; ukupne ulazne snage 9.3W, izlazni svjetlosni fluks svjetiljke 403lm, efikasnost svjetiljke 43lm/W, karakteristike izvora svijetla MacAdam 5, sočivo od polikarbonata, CRI>70, 100.000 radnih sati prije opadanja svjetlosnog fluksa na 95% inicijalne vrijednosti pri 25°C, Napravljena od livenog aluminijuma; boja kućišta bijela (RAL9016); Svetiljka sa lokalnim napajanjem iz autonomije 3 sata, sa automatskim testom (automatsko testiranje) preko svjetiljke, opcionalno centralno nadgledanje preko DALI, prikaz stanja svetiljke putem LED stanja; NFC interfejs za adresiranje, konfiguraciju i održavanje putem PROset olovke ili aplikacije PROset; obraćanje takođe moguće vizuelno ili putem EZ-obraćanja; napajanje: 220-240 V AC (+/- 10%), 50-60 Hz; SC1; Utični terminali za prolazno ožičenje do 2,5 mm²; Udarna čvrstoća: IK04; svjetiljka posjeduje CE/UKCA i ENEC sertifikat, dimenzije: Ø85 x 4 mm; težina: 0.7 kg; slična tipu RESCLITE PRO M MRCR ANT HP E3D WH, proizvođača Zumtobel ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Svjetiljka se isporucuje u kompletu sa izvorom svjetla, potrebnom opremom za rad. Ukupno za materijal i rad: | (P4) Procurement, delivery and installation of built-in LED lamps for anti-panic zone lighting with min. 0.5 lux in accordance with EN 1838; neutral white 4000K; total input power 9.3W, lamp output luminous flux 403lm, lamp efficiency 43lm/W, light source characteristics MacAdam 5, polycarbonate lens, CRI>70, 100,000 working hours before the luminous flux declines to 95% of the initial value at 25°C, Made from cast aluminum; housing color white (RAL9016); Luminaire with local power supply from autonomy of 3 hours, with automatic test (automatic testing) by the lamp, optional central monitoring by DALI, display of the status of the luminaire by LED status; NFC interface for addressing, configuration and maintenance by PROset pen or PROset application; addressing is also possible visually or by EZ-address; power supply: 220-240 V AC (+/- 10%), 50-60 Hz; SC1; Plug-in terminals for through wiring up to 2.5 mm²; Impact strength: IK04; the lamp has a CE/UKCA and ENEC certificate, dimensions: Ø85 x 4 mm; weight: 0.7 kg; similar to the type RESCLITE PRO M MRCR ANT HP E3D WH, manufactured by Zumtobel or the equivalent of another manufacturer with the same or better characteristic. The lamp is delivered with a light source and necessary equipment for work. Total for material and works: | kom/pcs |  | 64 | 0
27. |  | (P5) Nabavka, isporuka i ugradnja ugradne LED svetiljke za osvetljenje antipanik zona sa min. 1 lux u skladu sa EN 1838; neutralno bijela 4000K; ukupne ulazne snage 9.3W, izlazni svjetlosni fluks svjetiljke 436lm, efikasnost svjetiljke 47lm/W, karakteristike izvora svijetla MacAdam 5, sočivo od polikarbonata, CRI>70, 100.000 radnih sati prije opadanja svjetlosnog fluksa na 95% inicijalne vrijednosti pri 25°C, Napravljena od livenog aluminijuma; boja kućišta bijela (RAL9016); Svetiljka sa lokalnim napajanjem iz autonomije 3 sata, sa automatskim testom (automatsko testiranje) preko svjetiljke, opcionalno centralno nadgledanje preko DALI, prikaz stanja svetiljke putem LED stanja; NFC interfejs za adresiranje, konfiguraciju i održavanje putem PROset olovke ili aplikacije PROset; obraćanje takođe moguće vizuelno ili putem EZ-obraćanja; napajanje: 220-240 V AC (+/- 10%), 50-60 Hz; SC1; Utični terminali za prolazno ožičenje do 2,5 mm²; Udarna čvrstoća: IK04; svjetiljka posjeduje CE/UKCA i ENEC sertifikat, dimenzije: Ø85 x 4 mm; težina: 0.7 kg; slična tipu RESCLITE PRO M MRCR ESC HP E3D WH, proizvođača Zumtobel ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Svjetiljka se isporucuje u kompletu sa izvorom svjetla, potrebnom opremom za rad. Ukupno za materijal i rad: | (P5) Procurement, delivery and installation of built-in LED lamps for anti-panic zone lighting with min. 1 lux in accordance with EN 1838; neutral white 4000K; total input power 9.3W, lamp output luminous flux 436lm, lamp efficiency 47lm/W, light source characteristics MacAdam 5, polycarbonate lens, CRI>70, 100,000 working hours before the luminous flux declines to 95% of the initial value at 25°C, Made from cast aluminum; housing color white (RAL9016); Luminaire with local power supply from autonomy of 3 hours, with automatic test (automatic testing) via the lamp, optional central monitoring via DALI, display of the status of the luminaire via LED status; NFC interface for addressing, configuration and maintenance via PROset pen or PROset application; addressing is also possible visually or via EZ-address; power supply: 220-240 V AC (+/- 10%), 50-60 Hz; SC1; Plug-in terminals for through wiring up to 2.5 mm²; Impact strength: IK04; the lamp has a CE/UKCA and ENEC certificate, dimensions: Ø85 x 4 mm; weight: 0.7 kg; similar to the type RESCLITE PRO M MRCR ESC HP E3D WH, manufactured by Zumtobel or the equivalent of another manufacturer with the same or better characteristic. The lamp is delivered with a light source and necessary equipment for work. Total for material and works: | kom/pcs |  | 21 | 0
28. |  | (VS1) Nabavka, isporuka i ugradnja LED reflektora Plaza S7i, ulazne snage 12 W, svjetlosni fluks 768 lm, efikasnost svjetiljke 64lm/W, 80CRI, temperatura boje svijetla 4000K, stepena zaštite IP67, promjenljivi drajver. Plaza S7i je površinski postavljeni LED spoljni reflektor koji isporučuje 64 lm/W sa 80CRI 4000K LED diodama, karakteristike izvora svijetla MacAdam 3. Dizajniran za > 60.000 sati L90, težine 0.97 kg. Proizvod je dizajniran za ugradnju na temperaturi okoline -20°C do +50°C. Dostupni su dodatni dodaci - kaiš za drvo i šiljak za zemlju Svjetiljka je slična tipu PLAZA S7I 700-830 M BK 67 HF proizvodjača ACDC ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Ukupno za materijal i rad: | (VS1) Procurement, delivery and installation of Plaza S7i LED spotlight, input power 12 W, luminous flux 768 lm, lamp efficiency 64lm/W, 80CRI, light colour temperature 4000K, degree of protection IP67, variable driver. The Plaza S7i is a surface-mounted LED outdoor floodlight delivering 64 lm/W with 80CRI 4000K LEDs, light source characteristics MacAdam 3. Designed for > 60,000 hours L90, weight 0.97 kg. The product is designed for installation at an ambient temperature of -20°C to +50°C. Additional accessories are available - belt for wood and ground spike. The lamp is similar to the type PLAZA S7I 700-830 M BK 67 HF manufactured by ACDC. Total for material and works: | kom/pcs |  | 142 | 0
29. |  | Nabavka, isporuka i ugradnja ugradnog senzora pokreta radijusa 3 metara. Ukupno za materijal i rad. | Procurement, delivery and installation of a built-in motion sensor with a radius of 3 meters. Total for material and works. | kom/pcs |  | 38 | 0
III. |  | ELEKTRIČNA INSTALACIJA OSVJETLJENJA | ELECTRICAL LIGHTING INSTALLATION |  |  | Ukupno/Total | 0
IV. |  | INSTALACIONA OPREMA | INSTALLATION EQUIPMENT
30. |  | Nabavka, isporuka i ugradnja modularnog pribora sličan tipu LegrandMosaic, AVE,..., ili ekvivalent drugog proizvodjača istih ili boljih karakteristika bijela boja ugradna PVC kutija Ø60mm armatura 2M maska 2M priključnica 2P+E 16A, 2M bijela - 1 kom Ukupno za materijal i rad: | Procurement, delivery and installation of modular accessories similar to the type LegrandMosaic, AVE,..., or the equivalent of another manufacturer with the same or better characteristics white colour Built-in PVC box Ø60mm Armature 2M mask 2M socket2P+E 16A, 2M white - 1 pc UkupnTotal for material and work: | komplet/ set |  | 31 | 0
31. |  | Nabavka, isporuka i ugradnja modularnog pribora sličan tipu LegrandMosaic, AVE,..., ili ekvivalent drugog proizvodjača istih ili boljih karakteristika bijela boja ugradna PVC kutija 4M armatura 4M maska 4M priključnica 2P+E, 16A, 2M bijela - 2 kom Ukupno za materijal i rad: | Procurement, delivery and installation of modular accessories similar to the type LegrandMosaic, AVE,..., or the equivalent of another manufacturer with the same or better characteristics white colour built-in PVC box 4M armature 4M mask 4M socket 2P+E, 16A, 2M white - 2 pcs Total for material and work: | komplet/ set |  | 82 | 0
32. |  | Nabavka, isporuka i ugradnja modularnog pribora sličan tipu LegrandMosaic, AVE,..., ili ekvivalent drugog proizvodjača istih ili boljih karakteristika bijela boja ugradna PVC kutija Ø60mm armatura 2M maska 2M priključnica 2P+E, 16A, 2M bijela -1 kom-IP44 Ukupno za materijal i rad: | Procurement, delivery and installation of modular accessories similar to the type LegrandMosaic, AVE,..., or the equivalent of another manufacturer with the same or better characteristics white colour built-in PVC box Ø60mm armature 2M mask 2M socket 2P+E, 16A, 2M white - 1 pc - IP44 Total for material and work: | komplet/ set |  | 14 | 0
33. |  | Nabavka, isporuka i ugradnja trofazne priključnice 16A/400V, JUS N.EO.350. Priključnice su proizvod "Nopal"-Bačka Palanka ili slične drugog proizvođača. Ukupno za materijal i rad: | Procurement, delivery and installation of three-phase socket 16A/400V, JUS N.EO.350. The connectors are a "Nopal"-Bačka Palanka product or similar from another manufacturer. Total for material and works: | komplet/ set |  | 4 | 0
34. |  | Nabavka, isporuka i ugradnja modularnog pribora sličan tipu LegrandMosaic, AVE,..., ili ekvivalent drugog proizvodjača istih ili boljih karakteristika bijela boja ugradna PVC kutija Ø60mm armatura 2M maska 2M priključnica 2P+E 16A, 2M crvena - 1 kom Ukupno za materijal i rad: | Procurement, delivery and installation of modular accessories similar to the type LegrandMosaic, AVE,..., or the equivalent of another manufacturer with the same or better characteristics white colour built-in PVC box Ø60mm armature 2M mask 2M socket 2P+E, 16A, 2M RED - 1 pc Total for material and work: | komplet/ set |  | 4 | 0
35. |  | Nabavka, isporuka i ugradnja modularnog pribora sličan tipu LegrandMosaic, AVE,..., ili ekvivalent drugog proizvodjača istih ili boljih karakteristika bijela boja ugradna PVC kutija 4M armatura 4M maska 4M priključnica 2P+E, 16A, 2M crvena - 2 kom Ukupno za materijal i rad: | Procurement, delivery and installation of modular accessories similar to the Legrand Mosaic type, AVE, ..., or the equivalent of another manufacturer with the same or better characteristic white colour built-in PVC box 4M armature4M mask 4M connector 2P+E 16A, 2M red - 2 pc Total for material and work: | komplet/ set |  | 29 | 0
36. |  | Nabavka, isporuka i ugradnja modularnog pribora sličan tipu Legrand Mosaic, AVE, ..., ili ekvivalent drugog proizvodjača istih ili boljih karakteristika bijela boja ugradna PVC kutija 6M armatura 6M maska 6M priključnica 2P+E 16A, 2M crvena - 1 kom priključnica 2P, 16A, 1M crvena - 1 kom Ukupno za materijal i rad: | Procurement, delivery and installation of modular accessories similar to the Legrand Mosaic type, AVE, ..., or the equivalent of another manufacturer with the same or better characteristic white colour built-in PVC box 6M armature 6M mask 6M connector 2P+E 16A, 2M red - 1 pc connector 2P, 16A, 1M red - 1 pc Total for material and work: | komplet/ set |  | 31 | 0
37. |  | Nabavka, isporuka i ugradnja modularnog pribora sličan tipu Legrand Mosaic,..., ili ekvivalent drugog proizvodjača istih ili boljih karakteristika bijela boja ugradna PVC kutija 6M armatura 6M maska 6M priključnica 2P+E 16A, 2M crvena - 3 kom Ukupno za materijal i rad: | Procurement, delivery and installation of modular accessories similar to the Legrand Mosaic type,..., or the equivalent of another manufacturer with the same or better characteristic white colour built-in PVC box 6M armature 6M mask 6M socket 2P+E 16A, 2M red - 3 pcs Total for material and work: | komplet/ set |  | 27 | 0
38. |  | Nabavka, isporuka i ugradnja kutije 12M u koju se smještaju: priključnica 2P+E 16A, 2M zelena - 4 kom Ukupno za materijal i rad: | Procurement, delivery and installation of a 12M box that houses: Socket 2P+E 16A, 2M green - 4 pcs Total for material and work: | komplet/ set |  | 36 | 0
39. |  | Nabavka, isporuka i ugradnja kutije 8M u koju se smještaju: priključnica 2P+E 16A, 2M zelena - 4 kom priključnica 2P, 16A, 1M zelena - 1 kom Ukupno za materijal i rad: | Procurement, delivery and installation of the box 8M in which: Socket 2P+E 16A, 2M green - 4 pcs. Socket 2P, 16A, 1M green - 1 pc Total for material and work: | komplet/ set |  | 30 | 0
40. |  | Nabavka, isporuka i ugradnja modularnog pribora sličan tipu LegrandMosaic, AVE,..., ili ekvivalent drugog proizvodjača istih ili boljih karakteristika bijela boja ugradna PVC kutija Ø60mm armatura 2M dekorativna maska 2M obični prekidač 2M bijela - 1 kom Ukupno za materijal i rad: | Procurement, delivery and installation of modular accessories similar to the type LegrandMosaic, AVE,..., or the equivalent of another manufacturer with the same or better characteristic white colour built-in PVC box Ø60mm armature 2M decorative mask 2M ordinary switch 2M white - 1 pc Total for material and work: | komplet/ set |  | 58 | 0
41. |  | Nabavka, isporuka i ugradnja modularnog pribora sličan tipu LegrandMosaic, AVE,..., ili ekvivalent drugog proizvodjača istih ili boljih karakteristika bijela boja ugradna PVC kutija Ø60mm armatura 2M dekorativna maska 2M naizmjenični prekidač 2M bijela - 1 kom Ukupno za materijal i rad: | Procurement, delivery and installation of modular accessories similar to the type LegrandMosaic, AVE,..., or the equivalent of another manufacturer with the same or better characteristic white colour built-in PVC box Ø60mm armature 2M decorative mask 2M alternating switch 2M white - 1 pc Total for material and work: | komplet/ set |  | 10 | 0
42. |  | Nabavka, isporuka i ugradnja modularnog pribora sličan tipu LegrandMosaic, AVE,..., ili ekvivalent drugog proizvodjača istih ili boljih karakteristika bijela boja ugradna PVC kutija Ø60mm armatura 2M dekorativna maska 2M obični prekidač 1M bijela - 2 kom Ukupno za materijal i rad: | Procurement, delivery and installation of modular accessories similar to the type LegrandMosaic, AVE,..., or the equivalent of another manufacturer with the same or better characteristic white colour built-in PVC box Ø60mm armature 2M decorative mask 2M ordinary switch 1M white - 2 pcs Total for material and work: | komplet/ set |  | 3 | 0
43. |  | Nabavka, isporuka i ugradnja modularnog pribora sličan tipu Legrand Mosaic,..., ili ekvivalent drugog proizvodjača istih ili boljih karakteristika bijela boja ugradna PVC kutija 3M armatura 3M dekorativna maska 3M obični prekidač 1M bijela - 3 kom Ukupno za materijal i rad: | Procurement, delivery and installation of modular accessories similar to the Legrand Mosaic type,..., or the equivalent of another manufacturer with the same or better characteristic white colour built-in PVC box 3M armature 3M decorative mask 3M ordinary switch 1M white - 3 pcs Total for material and work: | komplet/ set |  | 30 | 0
44. |  | Nabavka, isporuka i ugradnja modularnog pribora sličan tipu Legrand Mosaic,..., ili ekvivalent drugog proizvodjača istih ili boljih karakteristika bijela boja ugradna PVC kutija 4M armatura 4M dekorativna maska 4M obični prekidač 1M bijela - 4 kom Ukupno za materijal i rad: | Procurement, delivery and installation of modular accessories similar to the Legrand Mosaic type,..., or the equivalent of another manufacturer with the same or better characteristic white colour built-in PVC box 4M armature 4M decorative mask 4M ordinary switch 1M white - 4 pcs Total for material and work: | komplet/ set |  | 1 | 0
45. |  | Nabavka, isporuka i ugradnja senzora temperature, stepena zaštite IP65. Senzor temperature se montira na fasadi objekta ili na krovu. Ukupno za materijal i rad: | Procurement, delivery and installation of temperature sensors, degree of protection IP65. The temperature sensor is installed on the facade of the building or the roof. Total for material and works: | komplet/ set |  | 2 | 0
IV. |  | INSTALACIONA OPREMA | INSTALLATION EQUIPMENT |  |  | Ukupno/Total | 0
V. |  | INSTALACIJA IZJEDNAČENJA POTENCIJALA | INSTALLATION OF POTENTIAL EQUALIZATION
46. |  | Isporuka finožičnog provodnika H07Z-K 1x10 mm2 sa žuto-zelenom izolacijom, polaganje i galvansko povezivanje metalnih masa (tehnološki i hidrotehnički uređaji, cijevi, razvodna tabla i metalne konstrukcije).Ukupno za materijal i rad: | Delivery of fine-wire conductor H07Z-K 1x10 mm2 with yellow-green insulation, installation and galvanic connection of metal masses (technological and hydro-technical devices, pipes, distribution boards and metal structures).Total for material and work: | m1 |  | 750 | 0
47. |  | Isporuka svog potrebnog materijala i izrada svih spojeva sa sabirnicom glavnog izjednačenja potencijala GIP u ormariću ispod »GRO« za izjednačenje potencijala objekta. Finožični provodnik H07Z-K 1x16 mm2 se polaže u HF samogasivim HDPE crijevima Ø 20/14mm od sabirnice GIP do centralnih jedinica sistema za klimatizaciju, cijevi vodovoda i kanalizacije, metalnih rukohvata stepeništa, ormara za smještaj vodomjera, hidranata, cijevi sprinkler instalacije, metalnih štokova vrata i ostalih metalnih masa u objektu koje ne pripadaju električnoj instalaciji. Povezivanje kabla na sabirnicu uraditi kablovskim papučicama i mesinganim zavrtnjem sa navrtkom i podmetačem, a u svemu prema tehničkom opisu.Ukupno za materijal i rad: | Procurement of material and making of all connections of the main potential equalization (GIP) by the busbar in the cabinet under »GRO« for object potential equalization. Fine-wire conductor H07Z-K 1x16 mm2 is installed in HF self-extinguishing HDPE hoses Ø 20/14mm from the busbar GIP to the central units of the air conditioning system, water pipes and sewerage, metal stair handrails, water gauge boxes, hydrant, pipe sprinkler installation, metal door elements and other metal masses in the building that do not belong to the electrical installation. According to the technical description, connect the cable to the busbar using cable lugs and a brass screw with a nut and a washer. Total for material and work: | m1 |  | 1500 | 0
48. |  | Isporuka i ugradnja metalnog ormarića sa sabirnicom Cu 30x4 mm za glavno izjednačenje potencijala objekta GIP, opremljenog sa priključnim stezaljkama. Ormarić se ugrađuje ispod glavnog razvodnog ormara GRO u prostoru prizemlja objekta. Ukupno za isporuku i rad računato po jednom ormariću sa sabirnicom GIP: | Delivery and installation of the metal cabinet with busbar Cu 30x4 mm for the primary equalization of the potential (GIP) of the building, equipped with connection clamps. The cabinet is installed under the main distribution cabinet GRO in the area of the ground floor of the building. Total for delivery and work calculated per one GIP busbar cabinet: | kom/pcs |  | 1 | 0
V. |  | INSTALACIJA IZJEDNAČENJA POTENCIJALA | INSTALLATION OF POTENTIAL EQUALIZATION |  |  | Ukupno/Total | 0
VI. |  | INSTALACIJA UZEMLJENJA I GROMOBRANA | INSTALLATION OF GROUNDING AND LIGHTNING PROTECTION
49. |  | Isporuka i ugradnja trake FeZn 25x4mm na mjestima naznačenim na planu instalacije za formiranje temeljnog uzemljivača I gromobranskih spusteva. Traku polagati prema tehničkom opisu i standardima za ovu vrstu radova. Ukupno za isporuku i rad: | Delivery and installation of FeZn 25x4mm tape in the places indicated on the installation plan to form the grounding conductor and lightning arresters. Install the tape according to this type of work's technical description and standards. Total for shipping and works: | m1 |  | 800 | 0
50. |  | Isporuka i montaža spojnih elemenata proizvođača Hermi ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Ukupno za isporuku i montažu: | Delivery and assembly of connecting elements,producer Hermi or the equivalent of another manufacturer with the same or better characteristic . Total for delivery and installation:
|  | loveći šiljak LOV | Hunting spike HUNTING | kom/pcs |  | 13 | 0
|  | KON žica-žica | KON wire-to-wire | kom/pcs |  | 191 | 0
|  | KON traka - traka | KON tape - tape | kom/pcs |  | 128 | 0
|  | KON traka - žica | KON tape - wire | kom/pcs |  | 26 | 0
|  | K-U-K kutija za ukrsni komad | K-U-K cross-piece box | kom/pcs |  | 128 | 0
|  | SON16 | SON16 | kom/pcs |  | 346 | 0
|  | SON17 | SON17 | kom/pcs |  | 854 | 0
|  | ZON03 | ZON03 | kom/pcs |  | 26 | 0
51. |  | Povezivanje svih metalnih masa na krovu sa prihvatnim vodom gromobranske instalacije. | Connecting all metal masses on the roof with the receiving installation of the lightning rod installation. | pauš./LS |  | 1 | 0
52. |  | Isporuka materijala i izvođenje spusnih provodnika od nerđajućeg čelika Fe/Zn Ø8 mm, prema planu gromobranske instalacije, sa izradom veza na uzemljivač i prihvatni sistem, a u svemu prema tehničkom opisu i planovima u prilogu projekta. Ukupno za materijal i rad: | Delivery of materials and execution of vertical conductors made of stainless steel Fe/Zn Ø8 mm, according to the layout of the lightning protection installation, with the connections to the grounding and receiving system, according to the technical description and plans attached to the Design. Total for material and works: | m1 |  | 260 | 0
53. |  | Isporuka materijala i izvođenje gromobranske instalacije okruglim provodnikom od nerđajućeg čelika FeZn Ø8mm, prema planu gromobranske instalacije, a u svemu prema tehničkom opisu i planovima u prilogu projekta. Ukupno za materijal i rad: | Delivery of materials and execution of the lightning rod installation with a round conductor made of stainless steel FeZn Ø8mm, according to the lightning rod installation plan and the technical description and drawings attached to the Design. Total for material and works: | m1 |  | 1260 | 0
VI. |  | INSTALACIJA UZEMLJENJA I GROMOBRANA | INSTALLATION OF GROUNDING AND LIGHTNING PROTECTION |  |  | Ukupno/Total | 0
VII. |  | NOSAČI KABLOVA - REGALI | THE CABLE TRAYS - RACKS
54. |  | Nabavka, isporuka i montaža perforiranih nosača kablova, sa brzom spojnicom, 60 x 300 x 3000 mm, napravljeni od pocinkovanog lima slični tipu RKSM E90 630 FS, proizvodjača OBO Bettermann ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Stavka obuhvata nabavku, isporuku i ugradnju nosača, konzoli neophodnih za ugradnju nosača kablova. Ukupno za materijal i rad: | Supply, delivery and installation of perforated cable trays, with quick coupling, 60 x 300 x 3000 mm, made of galvanized sheet similar to type RKSM E90 630 FS, manufactured by OBO Bettermann or the equivalent of another manufacturer with the same or better characteristic. The item includes the supply, delivery and installation of brackets, brackets necessary for the installation of cable trays. Total for material and works: | kom/pcs |  | 3 | 0
55. |  | Nabavka, isporuka i montaža perforiranih nosača kablova, sa brzom spojnicom, 60 x 200 x 3000 mm, napravljeni od pocinkovanog lima slični tipu RKSM E90 620 FS, proizvodjača OBO Bettermann ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Stavka obuhvata nabavku, isporuku i ugradnju nosača, konzoli neophodnih za ugradnju nosača kablova. Ukupno za materijal i rad: | Supply, delivery and installation of perforated cable trays, with quick coupling, 60 x 200 x 3000 mm, made of galvanized sheet similar to type RKSM E90 620 FS, manufactured by OBO Bettermann or the equivalent of another manufacturer with the same or better characteristic. The item includes the supply, delivery and installation of brackets, brackets necessary for the installation of cable trays. Total for material and works: | kom/pcs |  | 10 | 0
56. |  | Nabavka, isporuka i montaža T račve E90, horizontalna, sa Magic spojnicom, 60x300 mm, napravljena od pocinkovanog lima, proizvodjača OBO Bettermann ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Ukupno za materijal i rad: | Supply, delivery and installation of T piece E90, horizontal, with Magic connector, 60x300 mm, made of galvanized sheet, manufactured by OBO Bettermann or the equivalent of another manufacturer with the same or better characteristic. Total for material and works: | kom/pcs |  | 1 | 0
57. |  | Nabavka, isporuka i montaža T račve E90, horizontalna, sa Magic spojnicom, 60x200 mm, napravljena od pocinkovanog lima, proizvodjača OBO Bettermann ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Ukupno za materijal i rad: | Supply, delivery and installation of T piece E90, horizontal, with Magic connector, 60x200 mm, made of galvanized sheet, manufactured by OBO Bettermann or the equivalent of another manufacturer with the same or better characteristic. Total for material and works: | kom/pcs |  | 1 | 0
58. |  | Nabavka, isporuka i montaža krivine E90, horizontalna, sa Magic spojnicom, 60x300 mm, napravljena od pocinkovanog lima, proizvodjača OBO Bettermann ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Ukupno za materijal i rad: | Supply, delivery and installation of arc E90, horizontal, with Magic connector, 60x300 mm, made of galvanized sheet, manufactured by OBO Bettermann or the equivalent of another manufacturer with the same or better characteristics. Total for material and works: | kom/pcs |  | 2 | 0
59. |  | Nabavka, isporuka i montaža krivine E90, horizontalna, sa Magic spojnicom, 60x200 mm, napravljena od pocinkovanog lima, proizvodjača OBO Bettermann ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Ukupno za materijal i rad: | Supply, delivery and installation of arc E90, horizontal, with Magic connector, 60x200 mm, made of galvanized sheet, manufactured by OBO Bettermann or the equivalent of another manufacturer with the same or better characteristics. Total for material and works: | kom/pcs |  | 4 | 0
60. |  | Nabavka, isporuka i montaža perforiranih nosača kablova, sa brzom spojnicom, 60 x 300 x 3000 mm, napravljeni od pocinkovanog lima slični tipu MKS 630, proizvodjača OBO Bettermann ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Stavka obuhvata nabavku, isporuku i ugradnju nosača, konzoli neophodnih za ugradnju nosača kablova. Ukupno za materijal i rad: | Supply, delivery and installation of perforated cable trays, with quick coupling, 60 x 300 x 3000 mm, made of galvanized sheet similar to type MKS 630, manufactured by OBO Bettermann or the equivalent of another manufacturer with the same or better characteristics.The item includes the supply, delivery and installation of brackets, brackets necessary for the installation of cable trays. Total for material and works: | kom/pcs |  | 64 | 0
61. |  | Nabavka, isporuka i montaža perforiranih nosača kablova, sa brzom spojnicom, 60 x 200 x 3000 mm, napravljeni od pocinkovanog lima slični tipu MKS 620, proizvodjača OBO Bettermann ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Stavka obuhvata nabavku, isporuku i ugradnju nosača, konzoli neophodnih za ugradnju nosača kablova. Ukupno za materijal i rad: | Supply, delivery and installation of perforated cable trays, with quick coupling, 60 x 200 x 3000 mm, made of galvanized sheet similar to type MKS 620, manufactured by OBO Bettermann or the equivalent of another manufacturer with the same or better characteristic. The item includes the supply, delivery and installation of brackets, brackets necessary for the installation of cable trays. Total for material and works: | kom/pcs |  | 83 | 0
62. |  | Nabavka, isporuka i montaža perforiranih nosača kablova, sa brzom spojnicom, 60 x 100 x 3000 mm, napravljeni od pocinkovanog lima slični tipu MKS 610, proizvodjača OBO Bettermann ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Stavka obuhvata nabavku, isporuku i ugradnju nosača, konzoli neophodnih za ugradnju nosača kablova. Ukupno za materijal i rad: | Supply, delivery and installation of perforated cable trays, with quick coupling, 60 x 100 x 3000 mm, made of galvanized sheet similar to type MKS 610, manufactured by OBO Bettermann or the equivalent of another manufacturer with the same or better characteristic. The item includes the supply, delivery and installation of brackets, brackets necessary for the installation of cable trays. Total for material and works: | kom/pcs |  | 69 | 0
63. |  | Nabavka, isporuka i montaža T račve, horizontalna, sa Magic spojnicom, 60x300 mm, napravljena od pocinkovanog lima, proizvodjača OBO Bettermann ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Ukupno za materijal i rad: | Supply, delivery and installation of T piece, horizontal, with Magic connector, 60x300 mm, made of galvanized sheet, manufactured by OBO Bettermann or the equivalent of another manufacturer with the same or better characteristic. Total for material and works: | kom/pcs |  | 7 | 0
64. |  | Nabavka, isporuka i montaža T račve, horizontalna, sa Magic spojnicom, 60x200 mm, napravljena od pocinkovanog lima, proizvodjača OBO Bettermann ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Ukupno za materijal i rad: | Supply, delivery and installation of T piece, horizontal, with Magic connector, 60x200 mm, made of galvanized sheet, manufactured by OBO Bettermann or the equivalent of another manufacturer with the same or better characteristic. Total for material and works: | kom/pcs |  | 8 | 0
65. |  | Nabavka, isporuka i montaža T račve, horizontalna, sa Magic spojnicom, 60x100 mm, napravljena od pocinkovanog lima, proizvodjača OBO Bettermann ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Ukupno za materijal i rad: | Supply, delivery and installation of T piece, horizontal, with Magic connector, 60x100 mm, made of galvanized sheet, manufactured by OBO Bettermann or the equivalent of another manufacturer with the same or better characteristic. Total for material and works: | kom/pcs |  | 4 | 0
66. |  | Nabavka, isporuka i montaža krivine, horizontalna, sa Magic spojnicom, 60x300 mm, napravljena od pocinkovanog lima, proizvodjača OBO Bettermann ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Ukupno za materijal i rad: | Supply, delivery and installation of arc piece, horizontal, with Magic connector, 60x300 mm, made of galvanized sheet, manufactured by OBO Bettermann or the equivalent of another manufacturer with the same or better characteristic. Total for material and works: | kom/pcs |  | 1 | 0
67. |  | Nabavka, isporuka i montaža krivine, horizontalna, sa Magic spojnicom, 60x200 mm, napravljena od pocinkovanog lima, proizvodjača OBO Bettermann ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Ukupno za materijal i rad: | Supply, delivery and installation of arc piece, horizontal, with Magic connector, 60x200 mm, made of galvanized sheet, manufactured by OBO Bettermann or the equivalent of another manufacturer with the same or better characteristic. Total for material and works: | kom/pcs |  | 6 | 0
68. |  | Nabavka, isporuka i montaža krivine, horizontalna, sa Magic spojnicom, 60x100 mm, napravljena od pocinkovanog lima, proizvodjača OBO Bettermann ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Ukupno za materijal i rad: | Supply, delivery and installation of arc piece, horizontal, with Magic connector, 60x100 mm, made of galvanized sheet, manufactured by OBO Bettermann or the equivalent of another manufacturer with the same or better characteristic. Total for material and works: | kom/pcs |  | 4 | 0
69. |  | Nabavka, isporuka i montaža usponskih lestvičastih nosača kablova, sa lučnom obujmicom i letvama, 50 x 300 x 3000 mm, napravljeni od pocinkovanog lima slični tipu SLL 360 NS proizvodjača OBO Bettermann ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Ukupno za materijal i rad: | Supply, delivery and installation of riser ladder cable supports, with arc clamp and slats, 50 x 300 x 3000 mm, made of galvanized sheet similar to type SLL 360 NS by OBO Bettermann or the equivalent of another manufacturer with the same or better characteristics. Total for material and works | kom/pcs |  | 4 | 0
70. |  | Sitan montažni i nespecificirani materijal (anker vijci, torban vijci, plasticni pokloci za zavrsetak nosaca I sl.). | Minor assembly and unspecified material (anchor screws, bag screws, plastic covers for the end of the supports, etc.). | pauš./LS |  | 1 | 0
VII. |  | NOSAČI KABLOVA - REGALI | THE CABLE TRAYS - RACKS |  |  | Ukupno/Total | 0
VIII. |  | FISKULTURNA SALA | SPORTS HALL
71. |  | Isporuka materijala i izvođenje strujnih krugova osvjetljenja. Provodnici se polažu dijelom na zidu, dijelom na metalnoj krovnoj konstrukciji u tvrdim halogenfree cijevima odgovarajućeg prečnika. Instalaciju u svemu izvesti prema tehničkom opisu. Ukupno za materijal i rad u kompletu sa cijevima, obujmica i pratećom opremom neophodnom za polaganje provodnika: | Delivery of materials and execution of lighting circuits. The conductors are installed partly on the wall and partly on the metal roof structure in rigid halogen-free pipes of the appropriate diameter. Install according to the technical description. Total for material and work complete with pipes, clamps and accessory equipment necessary for routing conductors:
|  | N2XH-J 3x1,5 mm² | N2XH-J 3x1,5 mm² | m1 |  | 200 | 0
72. |  | Demontaža postojećih instalacija osvjetljenja u Sali. Stavka obuhvata demontažu svjetiljki i postojećih napojnih vodova za svjetiljke. Ukupno se demontira 42 svjetiljki i 8 reflektora na plafonu, 6 zidnih reflektora: | Dismantling of existing lighting installations in the Hall. The item includes dismantling the lamps and the existing power supply lines for the lights. A total of 42 lamps and eight ceiling reflectors, 6 wall reflectors are being dismantled: | komplet/ set |  | 56 | 0
73. |  | Nabavka, isporuka i montaža skele potrebne za demontažu postojećih svjetiljki i provodnika kao i za montažu novoprojektovanih svjetiljki i napojnih vodova od postojećeg ormara. Ukupno za materijal i rad: | Procurement, delivery and installation of the scaffolding required for dismantling existing lamps and conductors and for installing newly designed lights and power lines from the existing cabinet. Total for material and works: | komplet/ set |  | 1 | 0
74. |  | (S11) Nabavka,isporuka i ugradnja LED reflektora, ukupne ulazne snage 111.2W, izlazni svjetlosni fluks svjetiljke 17600lm, temperatura boje svijetla 4000K, efikasnost svjetiljke 158lm/W, optika pruza koeficijent blijestanja UGR<22 , karakteristike izvora svijetla MacAdam 2, 100.000 radnih sati prije opadanja svjetlosnog fluksa na 80% inicijalne vrijednosti pri 25°C, el. predspojni uredjaj integrisan unutar svjetiljke, kuciste svjetiljke izradjeno od visokokvalitetnog livenog aluminijuma otpornog na koroziju sa emajliranim zavrsetkom u bijeloj boji, stepena zastite IP66, dimenzija 518x414x109mm, tezine 7kg, svjetiljka posjeduje CE/UKCA, EPD i ENEC sertifikat, slična tipu CR2PL M17k-840 PC WB EVG WH proizvođača Zumtobe ili ekvivalent drugog proizvodjača istih ili boljih karakteristikal. Svjetiljka se isporucuje u kompletu sa izvorom svijetla, priborom za montazu i svom potrebnom opremom za rad. Ukupno za materijal i rad: | (S11) Procurement, delivery and installation of LED reflectors, total input power 111.2W, output luminous flux of the lamp 17600lm, light colour temperature 4000K, lamp efficiency 158lm/W, optics provide glare coefficient UGR<22, light source characteristics MacAdam 2, 100,000 working hours before the light flux decreases to 80% of the initial value at 25°C, electrical pre-switching device integrated inside the lamp, lamp housing made of high-quality corrosion-resistant cast aluminium with enamel finish in white colour, degree of protection IP66, dimensions 518x414x109mm, weight 7kg, the lamp has CE/UKCA, EPD and ENEC certificate, similar to type CR2PL M17k-840 PC WB EVG WH manufactured by Zumtobe or the equivalent of another manufacturer with the same or better characteristics. The lamp is delivered complete with a light source, mounting accessories and all necessary work equipment. Total for material and works: | kom/pcs |  | 12 | 0
75. |  | Nabavka, isporuka i montaža automatskih osigurača 10A, 1P, 6kA koji se smještaju u postojeći orman. Stavkom obuhvatiti i ugradnju 3 grebenaste sklopke 1-0, 16A, za montažu na vratima ormara kao i demontažu postojeće opreme koja se nalazi u ormaru a pripada zaštiti i kontroli postojeće instalacije osvjetljenja sale. Ukupno za materijal i rad: | Procurement, delivery and installation of automatic fuses 10A, 1P, and 6kA placed in the existing cabinet. The item also includes the installation of 3 cam switches 1-0, 16A, for mounting on the cabinet door and dismantling the existing equipment in the cabinet, which belongs to the protection and control of the existing hall lighting installation. Total for material and works: | komplet/ set |  | 3 | 0
76. |  | Isporuka i montaža spojnih elemenata proizvođača Hermi ili ekvivalent drugog proizvodjača istih ili boljih karakteristika. Ukupno za isporuku i montažu: | Delivery and installation of Hermi connecting elements or the equivalent of another manufacturer with the same or better characteristics. Total for delivery and installation:
|  | loveći šiljak LOV | hunting spike HUNTING | kom/pcs |  | 4 | 0
|  | KON žica-žica | KON wire-to-wire | kom/pcs |  | 14 | 0
|  | KON traka - žica | KON tape - wire | kom/pcs |  | 6 | 0
|  | K-U-K kutija za ukrsni komad | K-U-K cross-piece box | kom/pcs |  | 6 | 0
|  | SON16 | SON16 | kom/pcs |  | 156 | 0
|  | ZON03 | ZON03 | kom/pcs |  | 30 | 0
77. |  | Povezivanje svih metalnih masa na krovu sa prihvatnim vodom gromobranske instalacije. | Connecting all metal masses on the roof with the receiving water of the lightning rod installation. | pauš./LS |  | 1 | 0
78. |  | Isporuka materijala i izvođenje spusnih provodnika od nerđajućeg čelika Fe/Zn Ø8 mm, prema planu gromobranske instalacije, sa izradom veza na uzemljivač i prihvatni sistem, a u svemu prema tehničkom opisu i planovima u prilogu projekta. Ukupno za materijal i rad: | Delivery of materials and execution of down conductors made of stainless steel Fe/Zn Ø8 mm, according to the plan of the lightning protection installation, with the creation of connections to the grounding and receiving system, and in everything according to the technical description and methods attached to the project. Total for material and works: | m1 |  | 40 | 0
79. |  | Isporuka materijala i izvođenje gromobranske instalacije okruglim provodnikom od nerđajućeg čelika FeZn Ø8mm, prema planu gromobranske instalacije, a u svemu prema tehničkom opisu i planovima u prilogu projekta. Ukupno za materijal i rad: | Delivery of materials and execution of the lightning rod installation with a round conductor made of stainless steel FeZn Ø8mm, according to the lightning rod installation plan and the technical description and drawings attached to the project. Total for material and works: | m1 |  | 170 | 0
VIII. |  | FISKULTURNA SALA | SPORT HALL |  |  | Ukupno/Total | 0
IX. |  | ISPITIVANJE | TESTING
80. |  | Ispitivanje električnih instalacija jake struje škole sa pribavljanjem atesta | Testing of the school's high-voltage electrical installations with obtaining the certificate | pauš./LS |  | 1 | 0
81. |  | Ispitivanje gromobranske instalacije i uzemljenja škole sa pribavljanjem atesta. | Testing of the school's lightning protection installation and grounding with obtaining the certificate. | pauš./LS |  | 1 | 0
82. |  | Ispitivanje električnih instalacija jake struje sale sa pribavljanjem atesta | Testing of Hall's high-voltage electrical installations with obtaining the certificate | pauš./LS |  | 1 | 0
83. |  | Ispitivanje gromobranske instalacije i uzemljenja škole sa pribavljanjem atesta. | Testing of the school's lightning protection installation and grounding with obtaining the certificate | pauš./LS |  | 1 | 0
IX. |  | ISPITIVANJE | TESTING |  |  | Ukupno/Total | 0
X. |  | IZRADA PROJEKTA IZVEDENOG STANJA (ODRŽAVANJA) | PREPARATION OF AS-BUILT DESIGN (MAINTENANCE)
84. |  | IZRADA PROJEKTA IZVEDENOG STANJA (ODRŽAVANJA) | PREPARATION OF AS-BUILT DESIGN (MAINTENANCE) | pauš./LS |  | 1 | 0
X. |  | IZRADA PROJEKTA IZVEDENOG STANJA (ODRŽAVANJA) | PREPARATION OF AS-BUILT DESIGN (MAINTENANCE) |  |  | Ukupno/ Total | 0
3.1.1. |  | REKAPITULACIJA - JAKA STRUJA | SUMMARY HIGH VOLTAGE
I. |  | RAZVODNI ORMARI | DISTRIBUTION CABINETS |  |  |  | 0
II. |  | ELEKTRIČNA INSTALACIJA OPŠTE POTROŠNJE | ELECTRICAL INSTALLATION OF GENERAL CONSUMPTION |  |  |  | 0
III. |  | ELEKTRIČNA INSTALACIJA OSVJETLJENJA | ELECTRICAL LIFHTING INSTALLATION |  |  |  | 0
IV. |  | INSTALACIONA OPREMA | INSTAALLATION EQUIPMENT |  |  |  | 0
V. |  | INSTALACIJA IZJEDNAČENJA POTENCIJALA | INSTALLATION OF POTENTIAL EQUALIZATION |  |  |  | 0
VI. |  | INSTALACIJA UZEMLJENJA I GROMOBRANA | INSTALLATION OF GROUNDING AND LIGHTNING PROTECTION |  |  |  | 0
VII. |  | NOSAČI KABLOVA - REGALI | THE CABLE TRAYS - RACKS |  |  |  | 0
VIII. |  | FISKULTURNA SALA | SPORTS HALL |  |  |  | 0
IX. |  | ISPITIVANJE | TESTING |  |  |  | 0
X. |  | IZRADA PROJEKTA IZVEDENOG STANJA (ODRŽAVANJA) | PREPARATION OF AS-BUILT DESIGN (MAINTENANCE) |  |  |  | 0
3.1.1. |  | UKUPNO JAKA STRUJA | TOTAL HIGH VOLTAGE |  |  |  | 0

## 3.1.2. J.struja ur ter-HV-LAND
Program obrazovanja Crne Gore/ Education program of Montenegro
Predmjer - Izgradnja nove OŠ "Vladimir Nazor"/ Bill of Quantity - Construction of the new Elementary School "Vladimir Nazor" JAKA STRUJA UREĐENJE TERENA/ HIGH VOLTAGE - LANDSCAPING
br/ No | predmet / subject | NASLOV | DESCRIPTION | mj.jedinica/ unit | pred.cijena u eurima/ unit price € | Količina / Quantity | Cijena u eurima (bez PDV-a) / Amount in € (excl VAT)
(a) | (b) | (c) |  | ( d ) | (e) | (f) | (g=e*f)
3.1.2. |  | JAKA STRUJA UREĐENJE TERENA | HIGH VOLTAGE LANDSCAPING
|  | PREDMJER I PREDRAČUN JAKE STRUJE UREĐENJA TERENA | BILL OF QUANTITY OF HIGH VOLTAGE LANDSCAPING
I. |  | GRAĐEVINSKI RADOVI | CIVIL WORKS
1. |  | Pripremno-završni radovi, | Preparatory - final works | pauš./LS |  | 1 | 0
2. |  | Obilježavanje trase kablovskog voda radi iskopa rova. Ukupno za rad, računato za kompletnu trasu voda, dužine: | Marking the cable route for trench excavation. Total for work, calculated for the complete cable route, length: | m1 |  | 640 | 0
3. |  | Mašinski ili ručni iskop zemljanog rova dimenzija prema crtežima u prilogu projekta za polaganje kablova u rovu, u zemljištu do VII kategorije, prema planu u prilogu. Kategorija zemljišta je samo procjenjena, a ne i pouzdano utvrđena, pa podliježe izmjeni uz saglasnost nadzornog organa. Ukupno za rad i transport, računato po m³ iskopa: | Mechanical or manual excavation of the trench with dimensions according to the drawings attached to the Design for installing cables in the trench, in soil up to VII category, according to the attached drawings. The land category is only estimated and not reliably determined, so it is subject to change with the consent of the supervisor authority. Total for work and transport, calculated per m³ of excavation: | m3 |  | 256 | 0
4. |  | Mašinski ili ručni iskop zemljanog rova dimenzija 700x700x1000 mm (DxŠxV) za potrebe izrade betonskog temelja stuba, u zemljištu do VII kategorije, prema planu u prilogu. Kategorija zemljišta je samo procjenjena, a ne i pouzdano utvrđena, pa podliježe izmjeni uz saglasnost nadzornog organa. Ukupno za izradu ima 20 betonskih temelja. Ukupno za rad, računato po m³ iskopa: | Mechanical or manual excavation of the trench with dimensions of 700x700x1000 mm (LxWxH) for the concrete foundation of the pillar, in soil up to VII category, according to the attached plan. The land category is only estimated and not reliably determined, so it is subject to change with the consent of the Supervisor authority. There are a total of 20 concrete foundations to be made. Total for work, calculated per m³ of excavation: | m3 |  | 10 | 0
5. |  | Isporuka pijeska granulacije (0-4mm) i izrada posteljice kabla. Pri slobodnom polaganju kablova, prvo se razastire sloj pijeska debljine 10 cm, a nakon polaganja kablova i drugi sloj pijeska debljine takođe 10 cm. Pri izradi kablovske kanalizacije, prvo se razastre sloj pijeska (granulacije 0-4mm) debljine 10 cm, a nakon postavljanja kablovica i drugi sloj pijeska koji treba da ih prekriva za 10 cm. Ukupno za nabavku, transport i rad, računato po m³ korišćenog pijeska : | Delivery of granulated sand (0-4mm) and preparation of the cable subgrade. The 10 cm thick layer of sand is first spread, and after the cables are installed, the second layer of sand, also 10 cm thick, is spread. When making cable sewers, first, the layer of sand (granulation 0-4 mm) with the thickness of 10 cm is spread, and after laying the cable sewers, the second layer of sand should cover them by 10 cm. Total for procurement, transport and work, calculated per m³ of sand used: | m3 |  | 64 | 0
6. |  | Isporuka i postavljanje PVC trake za upozorenje sa odgovarajućim natpisom tipa T-E/80. Traka se polaže na oko 20 cm ispod gornje površine rova, prije zatrpavanja rova poslednjim slojem iskopa. Ukupno za nabavku i rad, računato po metru položene trake: | Delivery and installation of a PVC warning tape with a suitable inscription type T-E/80. The tape is laid about 20 cm below the upper surface of the trench before backfilling the trench with the last layer of backfilling. Total for procurement and work, calculated per meter of installed tape: | m1 |  | 650 | 0
7. |  | Isporuka i polaganje "gal"- štitnika mehaničke zaštite, iznad slobodno položenog kabla u rovu. Štitnici se polažu nakon razastiranja drugog sloja pijeska i to tako da se, po dužini, međusobno preklapaju za po desetak santimetara, prekrivajući kabal u potpunosti. Ukupno za nabavku, transport i rad, računato po položenom štitu (l = 1m): | Delivery and placing of "gal" - mechanical protection shield above the freely installed cable in the trench. The shields are placed after the second layer of sand has been spread. Pieces of shields overlap each other by ten centimetres, covering the cable completely. Total for procurement, transport and work, calculated per installed shield (l = 1m): | m1 |  | 715 | 0
8. |  | Isporuka i ugradnja kablovskih tablica sa naznakom tipa, presjeka i napona kabla sa imenom objekta gdje se nalazi drugi kraj kabla. Ukupno za nabavku, transport i rad, računato po ugrađenoj kablovskoj tablici: | Delivery and installation of cable plates indicating the type, section and voltage of the cable with the name of the facility where the other end of the cable is located. Total for procurement, transport and work, calculated according to the built-in cable table: | kom/pcs |  | 10 | 0
9. |  | Isporuka i ugradnja olovnih obujmica za obilježavanje kabla. Na olovnim obujmicama mora da bude utisnut tip, presjek, napon, godina polaganja i eventualno broj kablovskog voda u rovu. Obujmica se postavlja oko kabla na: *svakih 20m u pravoj liniji *prilikom skretanja trase kabla na 5m u oba pravca skretanja *ulazu i izlazu iz kablovske kanalizacije *na mjestu gdje se kablovski vod ukršta sa drugim podzemnim instalacijama *na mjestu ugradnje kablovske spojnice, stavljajući i godinu montaže spojnice *na svim ostalim mjestima gdje nadzorni organ smatra da je potrebno Ukupno za nabavku, transport i rad, računato po ugrađenoj olovnoj obujmici: | Delivery and installation of lead clamps for cable marking. The type, section, voltage, year of laying and possibly the number of the cable line in the trench must be stamped on the lead clamps. The clamp is placed around the cable at: every 20m in a straight line * When turning the cable route to 5 m in both directions of the turn *entrance and exit from the cable pipeline *at the point where the cable line crosses with other underground installations *at the place of installation of the cable connector, including the year of installation of the connector *in all other places where the Supervisor Authority determines it necessary; Total for supply, transport and works, calculated per installed lead clamp: | kom/pcs |  | 70 | 0
10. |  | Isporuka i ugradnja oznaka za obilježavanje trase kabla na regulisanom terenu. Oznaka se nalazi na nepravilnoj betonskoj kocki, a ugrađuje se pri završnim radovima na uređenju terena. na svakih 50 m po pravcu i na mjestima skretanja na po 5 m od centra skretanja u oba pravca, na mjestima ukrštanja kabla sa drugim inst. i ostalim mjestima prema tehničkom opisu, prema crtežima u prilogu. Oznake su standardne :betonska kocka sa mesinganom pločicom na kojoj je oznaka, proizvodnje "Elektroizgradnja" - Bajina Bašta (EBB) ili ekvivalentu istih ili boljih karakteristika. Ukupno za nabavku, transport i rad, računato po ugrađenoj oznaci: | Delivery and installation of signs for marking the cable route on regulated terrain. The sign is located on an irregular concrete cube, and it is installed during the finishing works on landscaping. Every 50 m in each direction and at the points of the turn at 5 m from the centre of the arch in both directions, at the points where the cable crosses with other installations and other places according to the technical description and according to the attached drawings. The markings are standard: the concrete cube with the brass tile on which the marking: is produced by "Elektroizgradnja" - Bajina Bašta (EBB) or the equivalent of another manufacturer with the same or better characteristic. Total for procurement, transport and work, calculated according to the built-in marking: | kom |  | 50 | 0
11. |  | Nabavka, isporuka i ugradnja kablovske kanalizacije-korugovanih cijevi HDPE, Ø75 mm, na mjestima polaganja kabla ispod betonskog postolja, betonskih površina kao i na mjestu ulaza kabla u objekat, prema crtežima u prilogu projekta, a plaća se po metru ugrađene cijevi. Ukupno za isporuku i montažu: | Procurement, transport and installation of cable sewerage-corrugated pipes HDPE, Ø75 mm. According to the attached design drawings, the pipes are placed where the cable is installed under the concrete base and at the point of cable entry into the facility. The pay per meter of installed pipe. Total for delivery and installation: | m1 |  | 140 | 0
12. |  | Nabavka, isporuka i ugradnja kablovske kanalizacije-korugovanih cijevi HDPE, Ø160 mm, na mjestima polaganja kabla ispod betonskih površina kao i na mjestu ulaza kabla u objekat, prema crtežima u prilogu projekta, a plaća se po metru ugrađene cijevi. Ukupno za isporuku i montažu: | Procurement, transport and installation of cable sewerage-corrugated pipes HDPE, Ø160 mm. According to the attached design drawings, the pipes are placed where the cable is installed under the concrete base and at the point of cable entry into the facility. The pay per meter of installed pipe. Total for delivery and installation: | m1 |  | 15 | 0
13. |  | Izrada zaštitnih mjera prilikom ukrštanja kablova sa drugim podzemnim objektima i instalacijama prema crtežu u prilogu i tehničkom opisu, paušalno: | Performing protective measures on positions crossing cables with other underground facilities and installations according to the attached drawing and technical description, flat rate: | kom/pcs |  | 19 | 0
14. |  | Izrada betonskih temelja stuba, beton MB20 dimenzija 700x700x1000mm (DxŠxV). Stavkom obuhvatiti ugradnju korugovanih cijevi HDPE Ø75 mm prilikom izrade betonskog temelja, kao i ugradnja anker vijaka koji su obuhvaćeni stavkom nabavke, isporuke i ugradnje stuba odgovarajućih dimenzija. Ukupno za izradu računato po komadu betonskog temelja: | Production of concrete foundations of the pillars, concrete MB20, dimensions 700x700x1000mm (LxWxH). The item includes the installation of corrugated HDPE Ø75 mm pipes during the construction of the concrete foundation and installing anchor bolts, which are included in the procurement, delivery and installation of pillars of appropriate dimensions. Total for construction calculated per piece of concrete foundation: | kom/pcs |  | 20 | 0
15. |  | Zatrpavanje kablovskog rova iskopom. Zatrpavanje se vrši u slojevima od po dvadesetak centimetara. Pri zatrpavanju uklanjati veće komade materijala oštrih ivica. Ukupno za rad, računato po m³ korištenog iskopa: | Backfilling of the cable trench with material from the excavation. Backfilling is done in layers of about twenty centimetres. When backfilling, remove larger pieces of material with sharp edges. Total for work, calculated per m³ of excavation used: | m3 |  | 192 | 0
16. |  | Uređenje zemljišta nakon obrade rovova sa odvozom viška materijala do deponije. Ukupno za rad i transport, računato sa udaljenošću deponije do 5 km, a plaća se po m³ viška iskopa. | Land levelling after processing the trenches with the removal of excess material to the landfill. The total for work and transport, calculated with a landfill distance of up to 5 km, is paid per m³ of leftover material from the excavation | m3 |  | 74 | 0
I. |  | GRAĐEVINSKI RADOVI | CIVIL WORKS |  |  | Ukupno/Total | 0
II. |  | ELEKTROMONTAŽNI RADOVI | ELECTRICAL ASSEMBLY WORKS
17. |  | Nabavka, transport i polaganje niskonaponskog energetskog kabla sa izolacijom i plaštom od PVC mase, prema DIN VDE 276-620. Kablovi se polažu na pripremljenoj posteljici kroz zemljani rov i djelimično kroz kablovsku kanalizaciju. Ovom pozicijom je obuhvaćeno: .razvlačenje kablova ·provlačenje kablova kroz kablovsku kanalizaciju ·izrada strujnih veza na oba kraja kabla | Procurement, transport and installation of low-voltage power supply cable with insulation and sheath made of PVC mass, according to DIN VDE 276-620. The cables are installed on the prepared subgrade through the trench and partly through the cable sewage. This position includes .cable placing ·pulling cables through the cable sewage ·making voltage connections at both ends of the cable
|  | tip kabla PP00 4x240 mm², 1/0.6kV | cable type PP00 4x240 mm², 1/0.6kV | m1 |  | 90 | 0
|  | tip kabla PP00 4x120 mm², 1/0.6kV | cable type PP00 4x120 mm², 1/0.6kV | m1 |  | 240 | 0
|  | tip kabla PP00-y 5x10 mm² | cable type PP00-y 5x10 mm², | m1 |  | 70 | 0
|  | tip kabla PP00-y 5x6 mm² | cable type PP00-y 5x6 mm², | m1 |  | 140 | 0
|  | tip kabla PP00-y 3x6 mm² | cable type PP00-y 3x6 mm², | m1 |  | 550 | 0
|  | tip kabla PP00-y 5x2.5 mm² | cable type PP00-y 5x2.5 mm², | m1 |  | 140 | 0
|  | tip kabla PP00-y 3x2.5 mm² | cable type PP00-y 3x2.5 mm², | m1 |  | 300 | 0
18. |  | Nabavka i montaža toploskupljajućih kablovskih glava i spojnica za unutrašnju-vanjsku montažu za postavljanje na napojnim kablovima NN mreže, proizvod Raychem ili ekvivalentu istih ili boljih karakteristika. Pod stavkom se podrazumijeva komplet montaža kablovskih glava tipa zajedno sa odgovarajućim kablovskim stopicama : | Procurement and installation of heat-shrinkable cable heads and connectors for internal-external assembly for installation on power cables of LV cable line, product Raychem or or the equivalent with the same or better characteristicr. The item is included the set of cable head assemblies of the type together with the corresponding cable feet:
|  | EPKT 0063 185-300 mm2 | EPKT 0063 185-300 mm2 | kom/pcs |  | 2 | 0
|  | EPKT 0047 70-150 mm2 | EPKT 0047 70-150 mm2 | kom/pcs |  | 6 | 0
|  | EPKT 0015 4-35 mm2 | EPKT 0015 4-35 mm2 | kom/pcs |  | 6 | 0
19. |  | Isporuka i ugradnja spojnica traka-traka JUS N.B4,936/III u kutiji za ukrsni komad "KUK" i zaliti bitumenom. Ukupno za isporuku i ugradnju: | Delivery and installation of tape-tape connectors JUS N.B4,936/III in the box for the cross-piece "KUK" coated with bitumen. Total for delivery and installation: | kom/pcs |  | 20 | 0
20. |  | Isporuka i polaganje trake od Fe/Zn 25x4mm u kablovski rov. Traka se polaže pri zatrpavanju rova, na dubini od oko 40 cm, nakon nanošenja prvog sloja iskopa. Stavka obuhvata i razvlačenje trake, nabavku ukrsnih komada “traka-traka” (JUS N.B4.936) i izradu međusobnih veza traka. Traka se u rovu polaže nasatice. Ukupno: | Delivery and laying of Fe/Zn tape 25x4mm in the cable trench. The tape is installed during the backfilling of the trench, at a depth of about 40 cm, after applying the first layer of backfilling. The item also includes the tape stretching, the procurement of "tape-tape" cross pieces (JUS N.B4.936) and the making of tape connections. The tape is installed in the trench on the narrow side. In total: | m1 |  | 650 | 0
21. |  | Ispitivanje izvedenih elektromontažnih radova, obezbjeđivanje sertifikata o efikasnosti sistema zaštite od opasnog napona dodira. mjerenje otpora uzemljenja, itd. | Testing of the performed electrical assembly works and provision of the certificate on the effectiveness of the protection system against dangerous contact voltage, earthing resistance measurement, etc. | pauš./LS |  | 1 | 0
22. |  | Ostali sitan instalacioni i montažni materijal: | Other minor installation and assembly material: | pauš./LS |  | 1 | 0
II. |  | ELEKTROMONTAŽNI RADOVI | ELECTRICAL ASSEMBLY WORKS |  |  | Ukupno/Total | 0
III. |  | ZAVRŠNI RADOVI | FINAL WORKS
23. |  | Izrada geodetskog snimanja trase položenih kablova. | The geodetic survey of the route of installed cables. | pauš./LS |  | 1 | 0
III. |  | ZAVRŠNI RADOVI | FINAL WORKS |  |  | Ukupno/Total | 0
IV. |  | ELEKTRIČNA INSTALACIJA OSVJETLJENJA | ELECTRICAL LIGHTING INSTALLATION
24. |  | (VS1) Nabavka isporuka i ugradnja LED reflektora, ukupne ulazne snage 27W, izlazni svjetlosni fluks svjetiljke 3523lm, efikasnost svjetiljke 120lm/W, temperatura boje svijetla 3000K, programabilni LED drajver, podešenza fiksni izlaz, pokreće 12 LED dioda na 700mA. Tijelo reflektora izrađeno od livenog aluminijuma (RAL7043), osovina izrađena od antracita (RAL7043), poklopac reflektora stkalo. Pričvršćivači reflektora izrađeni od nerđajućeg čelika sa antigalvanskim tretmanom, stepena zastite IP66, mehanicke zastite IK08, dimenzija Ø435x81, mase 6.6 kg, slična tipu CT S 12L70-730 NR CL2 T60F ANT proizvođača THORN ili ekvivalentu istih ili boljih karakteristika. Svjetiljka se montira na stub visine 5m. Svjetiljka se isporucuje u kompletu sa izvorom svijetla i svom potrebnom opremom za rad. Ukupno za materijal i rad: | (VS1) Procurement, delivery and installation of LED reflectors, total input power 27W, output luminous flux of the lamp 3523lm, lamp efficiency 120lm/W, light color temperature 3000K, programmable LED driver, set for fixed output, drives 12 LEDs at 700mA. Reflector body made of cast aluminum (RAL7043), shaft made of anthracite (RAL7043), reflector cover glass. Reflector fasteners made of stainless steel with anti-galvanic treatment, degree of protection IP66, mechanical protection IK08, dimensions Ø435x81, weight 6.6 kg, similar to type CT S 12L70-730 NR CL2 T60F ANT manufactured by THORN or equvivalent with the same or better characteristics. The lamp is mounted on the pole with the height of 5 m. The lamp is delivered complete with a light source and all necessary equipment for work. Total for material and works: | kom/pcs |  | 6 | 0
25. |  | (VS2) Nabavka isporuka i ugradnja stubne LED svjetiljke, ukupne ulazne snage 9W, izlazni svjetlosni fluks svjetiljke 403lm, efikasnost svjetiljke 45lm/W, temperatura boje svijetla 3000K, sa integrisanim LED drjaverom, kućište svjetiljke izrađeno od livenog aluminijuma (EN44300), praškasto obložen, teksturirani antracit (RAL7043) stepena zastite IP66, mehanicke zastite IK10, dimenzija 173x220x700mm, mase 6.49 kg, slična tipu RAB 1L20-830 WPC HF CL1 6K 700 ANT proizvođača THORN ili ekvivalentu istih ili boljih karakteristika. Ukupno za materijal i rad: | (VS2) Procurement, delivery and installation of a pole LED lamp, total input power 9W, output luminous flux of the lamp 403lm, lamp efficiency 45lm/W, light color temperature 3000K, with integrated LED driver, lamp housing made of cast aluminum (EN44300), powder coated , textured anthracite (RAL7043), degree of protection IP66, mechanical protection IK10, dimensions 173x220x700mm, weight 6.49 kg, similar to type RAB 1L20-830 WPC HF CL1 6K 700 ANT manufactured by THORN or the equivalent with the same or better characteristic. Total for material and works: | kom/pcs |  | 18 | 0
26. |  | (VS3) Nabavka isporuka i ugradnja LED reflektora, ukupne ulazne snage 39W, izlazni svjetlosni fluks svjetiljke 6287lm, efikasnost svjetiljke 161lm/W, temperatura boje svijetla 4000K, integrisan LED pretvarač konfigurisan za smanjenje snage, efikasan 3 sata prije i 5 sati posle ponoći. Tijelo reflektora izrađeno od livenog aluminijuma (EN AC-44300), svijetlo siva brušena tekstura (RAL9006). Kućište svjetiljke izrađeno od kaljenog stakla debljine 4mm, stepena zastite IP66, mehanicke zastite IK08, dimenzija 462x265x139mm, mase 6.24 kg, slična tipu AFP S 36L35-740 A6 BS 3550 CL2 GY proizvođača THORN ili ekvivalentu istih ili boljih karakteristika. Svjetiljka se montira na stub visine 8m Svjetiljka se isporucuje u kompletu sa izvorom svijetla i svom potrebnom opremom za rad. Ukupno za materijal i rad: | (VS3) Procurement, delivery and installation of LED reflectors, total input power 39W, output luminous flux of the lamp 6287lm, lamp efficiency 161lm/W, light color temperature 4000K, integrated LED converter configured to reduce power, effective 3 hours before and 5 hours after midnight. Reflector body made of cast aluminum (EN AC-44300), light gray brushed texture (RAL9006). Lamp housing made of 4mm thick tempered glass, degree of protection IP66, mechanical protection IK08, dimensions 462x265x139mm, weight 6.24 kg, similar to type AFP S 36L35-740 A6 BS 3550 CL2 GY manufactured by THORN or the equivalent with the same or better characteristic. The lamp is mounted on the pole with a height of 8 m. The lamp is delivered complete with a light source and all necessary equipment for work. Total for material and works: | kom/pcs |  | 11 | 0
27. |  | (VS4) Nabavka isporuka i ugradnja LED reflektora, ukupne ulazne snage 55W, izlazni svjetlosni fluks svjetiljke 8605lm, efikasnost svjetiljke 156lm/W, temperatura boje svijetla 4000K, integrisan LED pretvarač konfigurisan za smanjenje snage, efikasan 3 sata prije i 5 sati posle ponoći. Tijelo reflektora izrađeno od livenog aluminijuma (EN AC-44300), svijetlo siva brušena tekstura (RAL9006). Kućište svjetiljke izrađeno od kaljenog stakla debljine 4mm, stepena zastite IP66, mehanicke zastite IK08, dimenzija 462x265x139mm, mase 6.24 kg, slična tipu AFP S 36L50-740 A6 BS 3550 CL2 GY proizvođača THORN ili ekvivalentu istih ili boljih karakteristika. Svjetiljka se montira na stub visine 8m. Svjetiljka se isporucuje u kompletu sa izvorom svijetla i svom potrebnom opremom za rad. Ukupno za materijal i rad: | (VS4) Procurement, delivery and installation of LED reflectors, total input power 55W, output luminous flux of the lamp 8605lm, lamp efficiency 156lm/W, light color temperature 4000K, integrated LED converter configured to reduce power, effective 3 hours before and 5 hours after midnight. Reflector body made of cast aluminum (EN AC-44300), light gray brushed texture (RAL9006). Lamp housing made of 4mm thick tempered glass, degree of protection IP66, mechanical protection IK08, dimensions 462x265x139mm, weight 6.24 kg, similar to AFP S 36L50-740 A6 BS 3550 CL2 GY manufactured by THORN or the equivalent with the same or better characteristic. The lamp is mounted on the pole with a height of 8m. The lamp is delivered complete with a light source and all necessary equipment for work. Total for material and works: | kom/pcs |  | 6 | 0
28. |  | (VS5) Nabavka isporuka i ugradnja LED reflektora, ukupne ulazne snage 77W, izlazni svjetlosni fluks svjetiljke 11426lm, efikasnost svjetiljke 148lm/W, temperatura boje svijetla 4000K, integrisan LED pretvarač konfigurisan za smanjenje snage, efikasan 3 sata prije i 5 sati posle ponoći. Tijelo reflektora izrađeno od livenog aluminijuma (EN AC-44300), svijetlo siva brušena tekstura (RAL9006). Kućište svjetiljke izrađeno od kaljenog stakla debljine 4mm, stepena zastite IP66, mehanicke zastite IK08, dimenzija 462x265x139mm, mase 6.29 kg, slična tipu AFP S 36L70-740 A6 BS 3550 CL2 GY proizvođača Thorn ili ekvivalentu istih ili boljih karakteristika. Svjetiljka se montira na stub visine 5m. Svjetiljka se isporucuje u kompletu sa izvorom svijetla, priborom za montazu i svom potrebnom opremom za rad. Ukupno za materijal i rad: | (VS5) Procurement, delivery and installation of LED reflectors, total input power 77W, output luminous flux of the lamp 11426lm, lamp efficiency 148lm/W, light color temperature 4000K, integrated LED converter configured to reduce power, effective 3 hours before and 5 hours after midnight. Reflector body made of cast aluminum (EN AC-44300), light gray brushed texture (RAL9006). Lamp housing made of 4mm thick tempered glass, IP66 degree of protection, IK08 mechanical protection, dimensions 462x265x139mm, weight 6.29 kg, similar to AFP S 36L70-740 A6 BS 3550 CL2 GY manufactured by Thorn or the equivalent with the same or better characteristic. The lamp is mounted on the pole with a height of 5 m. The lamp is delivered complete with the light source, mounting accessories and all necessary equipment for work. Total for material and works: | kom/pcs |  | 2 | 0
29. |  | Nabavka, isporuka i ugradnja čeličnih konusnih stubova, čelika prema JUS.C.BO. 500/1988, klasa Č 0361 ili da bude bolji od njega, debljine min 3mm, okruglog poprečnog presjeka, zaštićen toplo pocinkovanog spolja i iznutra nanosom cinka, u skladu sa JUS EN ISO 1461, sa završnom- dekorativnom bojom RAL7043, elektrostatički nanesenom a zatim pečenom prema JUS EN 40- 4/1993. Stub treba da je predviđen za montažu na pripremljenom betonskom temelju, preko zavarene temeljne ploče (na dnu stuba), koja može biti ispupčena ili ravna ali mora da omogući efikasno odvođenje vode i ankera (sa maticama), ugrađenih u temelj pri njegovoj izradi. U donjem segmentu stuba treba da se nalazi otvor sa poklopcem i antivandal bravom, najmanjeg stepena zaštite IP 44, unutar kojeg treba da je ugrađen nosač za priključnu ploču kao i sa zavrtanj sa maticom za vezu stuba sa uzemljenjem. Uz stubove, proizvođač treba da isporuči i šablone za centrisanje ankera pri izradi temelja. Stub treba da je atestiran za pritisak vjetra od 90 daN/m2. Prilikom montaže stuba potrebno je provjeriti vertikalnost stuba iz dva upravna pravca. Ukupno računato po ugradjenom stubu visine 8m. Ekvivalent tipu CRS-A-9 proizvođača Amiga Kraljevo ili ekvivalentu istih ili boljih karakteristika. Ukupno za materijal i rad: | Procurement, delivery and installation of steel conical pillars, steel according to JUS.C.BO. 500/1988, class C 0361 or better than it, thickness min.3mm, round cross-section, protected by hot-dip galvanized outside and inside with zinc coating, in accordance with JUS EN ISO 1461, with final- decorative paint RAL7043, electrostatically applied and then baked according to JUS EN 40-4/1993. The item includes the construction of the concrete foundation for the steel conical pillar. The pillar should be designed for installing on the prepared concrete foundation covered by this item, by the welded base plate (at the bottom of the pillar), which can be convex or flat, but must allow for efficient drainage of water and anchors (with nuts), embedded in the foundation during its performing. In the lower segment of the pillar, there should be an opening with the cover and the anti-vandal lock, the minimum degree of protection IP 44, inside which the support for the connecting plate should be installed, and the screw with a nut for connecting the pillar to the ground. Along with the pillar, the manufacturer should also supply templates for centering the anchors when making the foundation. The pillar should be certified for wind pressure of 90 daN/m2. When assembling the pillar, it is necessary to check the verticality of the pillar from two vertical directions. In total, calculated by the installed pillar with a height of 8m. Equivalent to type CRS-A-9 manufactured by Amiga Kraljevo. Total for material and works: | kom/pcs |  | 12 | 0
30. |  | Nabavka, isporuka i ugradnja čeličnih konusnih stubova, čelika prema JUS.C.BO. 500/1988, klasa Č 0361 ili da bude bolji od njega, debljine min 3mm, okruglog poprečnog presjeka, zaštićen toplo pocinkovanog spolja i iznutra nanosom cinka, u skladu sa JUS EN ISO 1461, sa završnom- dekorativnom bojom RAL7043, elektrostatički nanesenom a zatim pečenom prema JUS EN 40- 4/1993. Stub treba da je predviđen za montažu na pripremljenom betonskom temelju, preko zavarene temeljne ploče (na dnu stuba), koja može biti ispupčena ili ravna ali mora da omogući efikasno odvođenje vode i ankera (sa maticama), ugrađenih u temelj pri njegovoj izradi. U donjem segmentu stuba treba da se nalazi otvor sa poklopcem i antivandal bravom, najmanjeg stepena zaštite IP 44, unutar kojeg treba da je ugrađen nosač za priključnu ploču kao i sa zavrtanj sa maticom za vezu stuba sa uzemljenjem. Uz stubove, proizvođač treba da isporuči i šablone za centrisanje ankera pri izradi temelja. Stub treba da je atestiran za pritisak vjetra od 90 daN/m2. Prilikom montaže stuba potrebno je provjeriti vertikalnost stuba iz dva upravna pravca. Ukupno računato po ugradjenom stubu visine 5m. Ekvivalent tipu KRS- A-6/60 proizvođača Amiga Kraljevo ili ekvivalentu istih ili boljih karakteristika. Ukupno za materijal i rad: | Procurement, delivery and installation of steel conical pillars, steel according to JUS.C.BO. 500/1988, class C 0361 or better than it, thickness min.3mm, round cross-section, protected by hot-dip galvanized outside and inside with zinc coating, in accordance with JUS EN ISO 1461, with final- decorative paint RAL7043, electrostatically applied and then baked according to JUS EN 40-4/1993. The item includes the construction of the concrete foundation for the steel conical pillar. The pillar should be designed for installing on the prepared concrete foundation covered by this item, by the welded base plate (at the bottom of the pillar), which can be convex or flat, but must allow for efficient drainage of water and anchors (with nuts), embedded in the foundation during its performing. In the lower segment of the pillar, there should be an opening with the cover and the anti-vandal lock, the minimum degree of protection IP 44, inside which the support for the connecting plate should be installed, and the screw with a nut for connecting the pillar to the ground. Along with the pillar, the manufacturer should also supply templates for centering the anchors when making the foundation. The pillar should be certified for wind pressure of 90 daN/m2. When assembling the pillar, it is necessary to check the verticality of the pillar from two vertical directions. In total, calculated by the installed pillar with a height of 5m high. Equivalent to type KRS-A-6/60 manufactured by Amiga Kraljevo. Total for material and works: | kom/pcs |  | 8 | 0
31. |  | Nabavka, isporuka i ugradnja lire predviđenu za montažu tri svjetiljke izabranog tipa dužine po 1m izrađenih od cijevi fi 60. Lira se postavlja na stubu na pozicijama datim na situacionom planu slične tipu LK-III proizvođača AMIGA Kraljevo ili ekvivalentu istih ili boljih karakteristika. Ukupno za materijal i rad: | Procurement, delivery and installation of the lyre designed for the installation of three lamps of the selected type, each 1m long, made of Ø 60 pipes. The lyre is placed on the pillar in the positions given on the layout, similar to the LK-III type manufactured by AMIGA Kraljevo or equivalent of the same or better characteristics. Total for material and works: | kom/pcs |  | 1 | 0
32. |  | Nabavka, isporuka i ugradnja lire predviđenu za montažu dvije svjetiljke izabranog tipa dužine po 1m izrađenih od cijevi fi 60. Lira se postavlja na stubu na pozicijama datim na situacionom planu slične tipu LK-II proizvođača AMIGA Kraljevo ili ekvivalentu istih ili boljih karakteristika. Ukupno za materijal i rad: | Procurement, delivery and installation of the lire designed for the installation of two lamps of the selected type, each 1m long, made of Ø 60 pipes. The lire is placed on the pillar in the positions given on the layout, similar to the LK-II type manufactured by AMIGA Kraljevo or equivalent of the same or better characteristics. Total for material and works: | kom/pcs |  | 3 | 0
33. |  | Nabavka, isporuka i ugradnja lire predviđenu za montažu jedne svjetiljke izabranog tipa dužine po 1m izrađenih od cijevi fi 60. Lira se postavlja na stubu na pozicijama datim na situacionom planu slične tipu LK-I proizvođača AMIGA Kraljevo ili ekvivalentu istih ili boljih karakteristika. Ukupno za materijal i rad: | Procurement, delivery and installation of the lire designed for the installation of one lamp of the selected type, each 1m long, made of Ø 60 pipes. The lire is placed on the pillar in the positions given on the layout, similar to the LK-I type manufactured by AMIGA Kraljevo or equivalent of the same or better characteristics. Total for material and works: | kom/pcs |  | 10 | 0
IV. |  | ELEKTRIČNA INSTALACIJA OSVJETLJENJA | ELECTRICAL LIGHTING INSTALLATION |  |  | Ukupno/ Total | 0
V. |  | DIZEL ELEKTRIČNI AGREGAT I ORMARI | DIESEL ELECTRIC GENERATOR (DEA) AND DISTRIBUTION BOXES
34. |  | Nabavka, transport i montaža dizel - električnog agregata (DEA) tipa Endress Group ESE 150 TBI ili ekvivalentu istih ili boljih karakteristika Podrazumijeva se nabavka DEA sledećih osnovnih podataka: -kontejnerskog tipa za spoljnu montažu, - kontinuirane snage na 50 Hz, Pin =150kVA (120kW) u "standby" rezimu rada, - dizel motor četvorotaktni, vodeno hlađeni sa 1500 ob/min - hladnjak i ventilator - mehaničko upravljanje - električni starter (anlaser) i alternator - normalni uslovi rada, suvi vazdušni filter - alternator sa jednim ležištem, IP 21, klasa izolacije H - standardni napon 400/230 V, 50 Hz - zavareni čelični ram sa anti-vibracionim postoljem - rezervoar za gorivo u postolju - ležišta za manipulaciju viljuškarom u postolju - savitljiva creva za dovod goriva i ventil za izbacivanje ulja iz kartera - baterija za startovanje sa kablovima i zaštitnom policom - standardni prigušivač zvuka i kompenzator dilatacije isporučuju se nepričvršćeni | Procurement, transport and installation of the diesel-electric unit (DEA) type Greenpower GP165S/B or the equivalent of the same or better characteristics.It is implied that DEA acquires the following basic data: -container type for external installation, - continuous power at 50 Hz, Pin = 150kVA (132kW) in "standby" operation mode, - four-stroke diesel engine, water-cooled with 1500 rev/min - cooler and fan - mechanical management - electric starter (anlaser) and alternator - normal operating conditions, dry air filter - alternator with one bearing, IP 21, insulation class H - standard voltage 400/230 V, 50 Hz - welded steel frame with anti-vibration base - fuel tank in the base - pallets for manipulating the forklift in the base - flexible hoses for fuel supply and a valve for ejecting oil from the crankcase - starter battery with cables and protective shelf - standard silencer and expansion compensator are delivered unattached
|  | predgrejač rashladne tečnostri motora za brzo opterećenje za automatske modele tehnička dokumentacija - modularna zvučno izolovana kućišta dostupna su na svim modelima i mogu se instalirati i naknadno sa komandnim ormarom za automatski rad. Sve ukupno sa svim radovima na montaži prema uputstvu. - Stavkom obuhvaćena izrada betonskog postolja i zaštitne ograde kao - Stavkom obuhvaćena izrada uzemljivača oko agregata - Stavkom obuhvaćena nabavka, isporuka, montaža i povezivanje ATS uredjaja u objektu škole. ATS je nominalne struje 250A. Ukupno za materijal i rad: | quick load engine coolant preheater for automatic models - technical documentation - modular sound-insulated housings are available on all models and can be installed subsequently with a control cabinet for automatic operation. All in total with all installation work according to the instructions. - The item includes the production of concrete base and protective fence - The item includes the production of earthing devices around the aggregate. - The item includes procurement, delivery, installation and connection of ATS devices in the school building. The ATS has a nominal current of 250A. Total for material and works: | kom/ pcs |  | 1 | 0
35. |  | Isporuka i ugradnja razvodnog ormara PMO-1, IP66 (fabričke ili radioničke izrade). Pod stavkom se podrazumijevaju i svi "sitni" elementi neophodni za ugradnju table, prekidača i ranžiranje kablova. u ormar se ugradjuje poluindirektno brojilo.(NAPOMENA: el.brojilo isporučuje Operator distributivnog sistema): U razvodnu tablu se ugrađuju sledeći elementi: | Delivery and installation of distribution box PMO-1, IP66 (factory or workshop production). The item also includes all "small" elements necessary for the installation of the panel, switches and cable routing. The semi-indirect meter is installed in the boxt. (NOTE: the electric meter is supplied by the Distribution System Operator). The following elements are installed in the switchboard:
|  | Rastavljač INS 320A | Disconnector INS 250A | kom/ pcs |  | 1
|  | strujni transformator 400/5A | current transformer 200/5A | kom/ pcs |  | 3
|  | Rastavljači sa osiguračima 160/125A | Disconnectors with fuses 160/125A | kom/ pcs |  | 1
|  | Rastavljači sa osiguračima 400/315A | Disconnectors with fuses 250/200A | kom/ pcs |  | 1
|  | Katodni odvodnici V50-3+NPE 280 OBO-Betterman | Cathodic arresters V50-3+NPE 280 OBO-Betterman | kom/ pcs |  | 1
|  | Stavkom obuhvatiti sabirnice, redne stezaljke, POK kanali, plastične etikete, pertinaks, natpisne ploče, bakarne pletenice, uvodnice za kablove, jednopolna šema, džep za jednopolnu šemu i drugi potrebni sitni materijla neophodan za ugradnju ormana. Ukupno za materijal i rad: | The item includes busbars, row clamps, POK channels, plastic labels, pertinax, nameplates, copper braids, cable glands, single-pole scheme, pocket for single-pole scheme and other necessary small materials necessary for the installation of the cabinet. Total for material and works: | kom/ pcs |  | 1 | 0
36. |  | Isporuka i ugradnja razvodnog ormara PMO-2 i PMO-3, IP66 (fabričke ili radioničke izrade). Pod stavkom se podrazumijevaju i svi "sitni" elementi neophodni za ugradnju table, prekidača i ranžiranje kablova. u ormar se ugradjuje poluindirektno brojilo.(NAPOMENA: el.brojilo isporučuje Operator distributivnog sistema): U razvodnu tablu se ugrađuju sledeći elementi: | Delivery and installation of distribution box PMO-2 and PMO-3, IP66 (factory or workshop production). The item also includes all accessory elements necessary for installing panels, switches and cable routing. The semi-indirect electrical meter is installed in the cabinet. (NOTE: the Distribution System Operator supplies the electric meter): The following elements are installed in the switchboard:
|  | Rastavljač INS 250A | Disconnector INS 250A | kom/ pcs |  | 1
|  | strujni transformator 200/5A | Current transformer 200/5A | kom/ pcs |  | 3
|  | Rastavljači sa osiguračima 160/125A | Disconnectors with fuses 160/125A | kom/ pcs |  | 1
|  | Rastavljači sa osiguračima 250/200A | Disconnectors with fuses 250/200A | kom/ pcs |  | 1
|  | Katodni odvodnici V50-3+NPE 280 OBO-Betterman | Cathodic arresters V50-3+NPE 280 OBO-Betterman | kom/ pcs |  | 1
|  | Stavkom obuhvatiti sabirnice, redne stezaljke, POK kanali, plastične etikete, pertinaks, natpisne ploče, bakarne pletenice, uvodnice za kablove, jednopolna šema, džep za jednopolnu šemu i drugi potrebni sitni materijla neophodan za ugradnju ormana. Ukupno za materijal i rad: | The item includes busbars, row clamps, POK channels, plastic labels, pertinax, nameplates, copper braids, cable glands, single-pole scheme, pocket for single-pole scheme and other necessary small materials necessary for the installation of the cabinet. Total for material and works: | kom/ pcs |  | 2 | 0
V. |  | DIZEL ELEKTRIČNI AGREGAT I ORMARI | DIESEL ELECTRIC GENERATOR (DEA) AND DISTRIBUTION BOXES |  |  | Ukupno/Total | 0
3.1.2. |  | REKAPITULACIJA - JAKA STRUJA UREĐENJE TERENA | SUMMARY - HIGH VOLTAGE LANDSCAPING
I. |  | GRAĐEVINSKI RADOVI | CIVIL WORKS |  |  |  | 0
II. |  | ELEKTROMONTAŽNI RADOVI | ELECTRICAL ASSEMBLY WORKS |  |  |  | 0
III. |  | ZAVRŠNI RADOVI | FINAL WORKS |  |  |  | 0
IV. |  | ELEKTRIČNA INSTALACIJA OSVJETLJENJA | ELECTRICAL LIGHTING INSTALLATION |  |  |  | 0
V. |  | DIZEL ELEKTRIČNI AGREGAT I ORMARI | DIESEL ELECTRIC GENERATOR (DEA) AND DISTRIBUTION BOXES |  |  |  | 0
3.1.2. |  | UKUPNO JAKA STRUJA UREĐENJE TERENA | SUMMARY - HIGH VOLTAGE LANDSCAPING |  |  |  | 0

## 3.2. Slaba struja-LOW VOLT
Program obrazovanja Crne Gore/ Education program of Montenegro
Predmjer - Izgradnja nove OŠ "Vladimir Nazor"/ Bill of Quantity - Construction of the new Elementary School "Vladimir Nazor" SLABA STRUJA / LOW VOLTAGE INSTALLATION
br/ No | predmet / subject | NASLOV | DESCRIPTION | mj.jedinica/ unit | pred.cijena u eurima/ unit price € | Količina / Quantity | Cijena u eurima (bez PDV-a) / Amount in € (excl VAT)
(a) | (b) | (c) |  | ( d ) | (e) | (f) | (g=e*f)
3.2. |  | SLABA STRUJA | LOW VOLTAGE INSTALLATION
|  | PREDMJER I PREDRAČUN SLABE STRUJE | BILL OF QUANTITY OF LOW VOLTAGE
I. |  | GRAĐEVINSKI RADOVI | CIVIL WORKS
1. |  | Pripremno-završni radovi | Preparatory-fnal works | pauš/LS |  | 1 | 0
2. |  | Obilježavanje trase i iskop rova dimenzija 0.4x0.6m, za potrebe polaganja PEHD cijevi Ø110mm od postojećeg TK priključka do RACK ormara na etaži podruma u skladu sa UTU za potrebe priključenja na postojeću TK infrastrukuturu. U kanal predvidjeti podlogu od pijeska visine 0.1m na koju se na dubini 0.5m postavljaju cijevi i zatrpavaju tamponom 0.1m od pijeska i ostatka zemlje. Iskop se vrši ručno, u zemljištu III i IV kategorije. Ukupno za rad, računato po m³ izvršenog iskopa: | Marking the route and excavation of the trench, dimensions 0.4x0.6m, for installing PEHD pipes Ø110mm from the TC connection of the existing TC infrastructure to the RACK cabinet on the basement floor, following UTU. Provide the 0.1m thick sand subgrade in the channel, on which the pipes are placed at a depth of 0.5m and covered with the 0.1m sand layer. Backfilling the rest of the trench is by the material from the excavation. Excavation is done manually in the soil of categories III and IV. Total for work, calculated per m³ of performed excavation: | m3 |  | 96 | 0
3. |  | Nabavka, isporuka i razastiranje pijeska granulacije 0-4mm u kablovskim rovovima. Razastiru se dva sloja pijeska, debljine po 10cm, prije i poslije polaganja cijevi. Pijesak se polaže cijelom širinom rova. Ukupno za materijal i rad, računato po m³ pijeska: | Procurement, delivery and spreading of 0-4mm sand in cable trenches. Two layers of sand, each 10 cm thick, are spread below and over the installed pipes. Sand is spread across the entire width of the trench. Total for material and work, calculated per m³ of sand: | m3 |  | 48 | 0
4. |  | Nabavka, isporuka i polaganje PEHD cijevi Ø110mm u rov, komplet sa odstojnim držačima i gumenim prstenovima za dihtovanje pri nastavljanju cijevi kao i gumenim čepovima za zatvaranje rezervnih kablovica. Kroz PEHD cijev će se provući fiber optički kabl potrebnog kapaciteta od postojećeg TK priključka do RACK ormara u objektu. Obračun vršiti po dužnom metru. Ukupno za materijal i rad: | Procurement, delivery and installation of PEHD pipes Ø110mm in the trench, with spacer holders, rubber rings for sealing when continuing the pipes, and rubber plugs for closing reserve cables. A fibre optic cable of the required capacity will be passed through the PEHD pipe from the existing TCK connection to the RACK cabinet in the facility. The calculation should be done with the required meter. Total for material and works: | m1 |  | 350 | 0
5. |  | Nabavka, isporuka i polaganje HDPE cijevi Ø40mm u rov, komplet sa odstojnim držačima i gumenim prstenovima za dihtovanje pri nastavljanju cijevi kao i gumenim čepovima za zatvaranje rezervnih kablovica. Kroz HFPE cijev će se provući kabal za vezu između objekta škole i fiskulturne sale koji se tiče sistema za automatsku dojavu požara. Obračun vršiti po dužnom metru. Ukupno za materijal i rad: | Procurement, delivery and installation of HDPE pipes Ø40mm in the trench, with spacer holders, rubber rings for sealing when continuing the pipes, and rubber plugs for closing reserve cables.The cable for connecting the school building and the Sports Hall regarding the automatic fire alarm system will be passed through the HDPE pipe. The calculation should be done with the required meter. Total for material and works: | m1 |  | 50 | 0
6. |  | Nabavka, isporuka i polaganje upozorne trake od mekanog polivinilhlorida koja se postavlja na 20 cm od površine zemlje. Ukupno za materijal i rad, računato po metru trake: | Procurement, delivery and installation of warning tape made of soft polyvinyl chloride, placed on the dept 20 cm from the ground surface. Total for material and works, calculated per meter of tape: | m1 |  | 350 | 0
7. |  | Zatrpavanje kablovskog rova. Zatrpavanje se vrši u slojevima od po petnaestak centimetara. Pri zatrpavanju uklanjati veće komade materijala oštrih ivica. Obračunom obuhvatiti odvoz viška materijla, kao i dovođenje površina u prvobitno stanje. Ukupno za rad, računato po m³ korišćenog iskopa: | Backfilling of the cable trench. Backfilling is done in layers of about fifteen centimetres. When backfilling, remove more significant pieces of material with sharp edges. The calculation includes the removal of excess material and the preparation of surfaces to their original condition. Total for work, calculated per m³ of excavation used: | m3 |  | 48 | 0
8. |  | Nabavka, isporuka i ugradnja čepova za zatvaranje HDPE cijevi Ø 110mm. Ukupno za materijal i rad: | Procurement, delivery and installation of plugs for closing HDPE pipes Ø 110mm. Total for material and works: | kom/pcs |  | 10 | 0
9. |  | Izrada AB(Q335) okna unutrašnjih dimenzija 100x100x100cm: iskop rupe za okno,odvoz šuta na deponiju,izrada okna(d=15cm(zidova, i donje ploče), d=20cm gornje ploče) sa ugradnjom čeličnog tk poklopca sa ramom (rad+materijal bez tk poklopca sa ramom). | Production of RC (reinforcement mesh Q335) manhole with internal dimensions of 100x100x100cm: excavation of the hole, transport of material to the landfill, production of the manhole (d=15cm (walls and bottom plate), d=20cm top plate) with the installation of a steel TC cover with the frame (work+ material without TC cover with frame). | kom/pcs |  | 4 | 0
10. |  | Nabavka, isporuka i ugradnja Lakog TK poklopca 60x60cm sa ramom.. Ukupno za materijal i rad: | Procurement, delivery and installation of TC cover for light traffic, dimensions 60x60cm with frame. Total for material and works: | kom/pcs |  | 4 | 0
11. |  | Nabavka, isporuka i ugradnja oznaka za obilježavanje trase kablovskog voda na regulisanom terenu. Oznaka se ugrađuje pri završnim radovima na uređenju terena na svakih 50 m po pravcu i na mjestima skretanja na po 5m od centra skretanja u oba pravca. Oznake su standardne: betonska kocka sa mesinganom pločicom na kojoj je oznaka, proizvodnje “Elektroizgradnja” - Bajina Bašta (EBB) ili slična drugog proizvođača. Ukupno za materijal i rad, računato po ugrađenoj oznaci za regulisani teren: | Procurement, delivery and installation of signs for marking the cable line route on regulated terrain. The sign is installed during the finishing works on landscaping every 50 m in each direction and at the turning points at 5 m from the turning centre in both directions. The markings are standard: a concrete cube with a brass plate on which a marking is produced by "Elektroizgradnja" - Bajina Bašta (EBB) or similar by another manufacturer. Total for material and works, calculated according to the built-in mark of cable line on regulated land: | kom/pcs |  | 5 | 0
12. |  | Izrada zaštitnih mjera prilikom ukrštanja kablova sa drugim podzemnim objektima i instalacijama prema crtežu u prilogu i tehničkom opisu, paušalno: | Implementation of protective measures when crossing cables with other underground facilities and installations according to the attached drawing and technical description, flat rate: | pauš/LS |  | 1 | 0
|  | Kako projektant nije imao uvid u TK infrastrukturu, tačnu poziciju planiranog TK priključka treba utvrditi prilikom izvođenja radova. Dužina rova i cijevi je data paušalno, a stvarne dužine je potrebno utvrditi prilikom izvođenja radova. | Since the designer had no insight into the existing TC infrastructure, the exact position of the designed TC connection should be determined during the execution of the works. Therefore, the length of the trench and pipe is given as a flat rate, and the actual lengths must be determined during the execution of the works.
I. |  | GRAĐEVINSKI RADOVI | CIVIL WORKS |  |  | Ukupno/Total | 0
II. |  | INSTALACIJA STRUKTURNO KABLOVSKOG SISTEMA (SKS) | INSTALLATION OF STRUCTURAL CABLE SYSTEM (SCS)
13. |  | Nabavka, isporuka i ugradnja stojećeg RACK ormara karakteristika 42U/19" rek orman stojeći, staklena vrata sa bravom, prstenovi za vertikalno vođenje kablova, točkići i nožice sa nivelacijom, prednje i zadnje šine 19" sa brojevima unita, dim. 800x800x2000mm, do 800kg Ukupno za materijal i rad: | Supply, delivery and installation of standing RACK cabinet with the following characteristics: 42U/19" standing rack cabinet, glass door with lock, rings for vertical cable routing, wheels and feet with levelling, front and back rails 19" with unit numbers, dim. 800x800x2000mm, up to 800kg Total for material and work: | kom/pcs |  | 4 | 0
14. |  | Nabavka, isporuka i ugradnja fiber optičkog patch panela 19"/1U sa 24 slota za duplex SC/ST/LC adaptere do 48 SC i/ili 96 LC konektora sa slide mehanizmom i splajs kasetama. U cijenu je uračunato i splajsovanje optičkih kablova. Ukupno za materijal i rad: | Procurement, delivery and installation of a fibre optic patch panel 19"/1U with 24 slots for duplex SC/ST/LC adapters up to 48 SC and/or 96 LC connectors with the slide mechanism and splice cassettes. The price includes the splicing of optical cables. Total for material and works: | kom/pcs |  | 2 | 0
15. |  | Nabavka, isporuka i ugradnja patch panela za smještanje u RACK ormare, 1U/19" sa 24xRJ-45 FTP kat. 6 Fully Shielded, LSA reglete, držač kablova sa zadnje strane sa buksnom za uzemljenje (fiksni portovi). U cijenu je uračunato i terminiranje kablova. Ukupno za materijal i rad: | Supply, delivery and installation of patch panels for placement in RACK cabinets, 1U/19" with 24xRJ-45 FTP cat. 6 Fully Shielded, LSA shunting rail, cable holder on the back with grounding socket (fixed ports). The price includes cable termination Total for material and works: | kom/pcs |  | 20 | 0
16. |  | Nabavka, isporuka i ugradnja 230V razvodnog panela 1U/19" sa 7 utičnih mjesta, prekidačem, prenaponskom zaštitom i kablom 2m sa utikačem. Ukupno za materijal i rad: | Procurement, delivery and installation of the 230V distribution panel 1U/19" with 7 sockets, switch, overvoltage protection and 2m cable with plug. Total for material and work: | kom/pcs |  | 10 | 0
17. |  | Nabavka, isporuka i ugradnja police na izvlačenje - slide mehanizam za RACK. Ukupno za materijal i rad: | Supply, delivery and installation of the pull-out shelf-slide mechanism for RACK. Total for material and works: | kom/pcs |  | 5 | 0
18. |  | Nabavka, isporuka i ugradnja organizera kablova sa prstenovima, obostrani 1U/19". Ukupno za materijal i rad: | Supply, delivery and installation of cable organizer with rings, both sides 1U/19". Total for materials and works: | kom/pcs |  | 20 | 0
|  | NAPOMENA: Dio RJ-45 telekomunikacionih modula iz predmjera slabe struje se montira u instalacione kutije definisane predmjerom jake struje. | NOTE: Part of the RJ-45 telecommunication modules from the low current B of Q is installed in the installation boxes defined by the high voltage B of Q.
19. |  | Nabavka, isporuka i ugradnja dvomodularnog instalacionog pribora na pozicijama iz projekta SS, proizvođača Legrand Mosaic, Ave ili slično: PVC kutija 2M za montažu u zid Nosač 2M Dekorativna maska 2M Slijepi modul 1kom Ukupno za materijal i rad: | Procurement, delivery and installation of two-modular installation accessories in positions from the Low Voltage design, manufactured by Legrand Mosaic, Ave or similar: PVC box 2M for wall mounting; Bracket 2M; Decorative mask 2M; Blind module 1pc; Total for material and works | kom/pcs |  | 38 | 0
20. |  | Simplex patch cord kabl LC/UPC - LC/UPC | Simplex patch cord cable LC/UPC - LC/UPC | kom/pcs |  | 22 | 0
21. |  | Isporuka, ugradnja i povezivanje Firewall router-a u rack-u podruma skole. RB4011iGS+RM RouterBOARD 4011iGS+ with Annapurna Alpine AL21400 Cortex A15 CPU (4-cores, 1.4GHz per core), 1GB RAM, 10xGbit LAN, 1xSFP+ port, RouterOS L5, desktop case, rackmount ears, PSU | Delivery, installation and connection of the Firewall router in the rack in the school's basement. RB4011iGS+RM RouterBOARD 4011iGS+ with Annapurna Alpine AL21400 Cortex A15 CPU (4-cores, 1.4GHz per core), 1GB RAM, 10xGbit LAN, 1xSFP+ port, RouterOS L5, desktop case, rackmount ears, PSU | kom/pcs |  | 1 | 0
22. |  | Isporuka i montaža rekabilnog UPS uređaja snage 1700 VA, sličan tipu SOCOMEC NPR-1700-RT UPS. 1700VA/1350W 230V 50/60Hz AVR, Sine wave, LCD, RJ45, 1xUSB, 1xRS232 | Delivery and installation of the 1700 VA rechargeable UPS device, similar to the SOCOMEC NPR-1700-RT UPS type. 1700VA/1350W 230V 50/60Hz AVR, Sine wave, LCD, RJ45, 1xUSB, 1xRS232. | kom/pcs |  | 1 | 0
23. |  | Isporuka i montaža bi direkcionog SFP modula SFP 1.25G TX 1310nm 10km DDM. SFP primopredajnici su visokih performansi, koji podržavaju dvostruku brzinu prenosa podataka od 1,25Gbps/1,0625Gbps i 20km udaljenosti prenosa sa SMF-om | Delivery and installation of the directional SFP module SFP 1.25G TX 1310nm 10km DDM. SFP transceivers are high-performance, supporting dual data rates of 1.25Gbps/1.0625Gbps and 20km transmission distance with SMF | kom/pcs |  | 10 | 0
24. |  | Isporuka i montaža bi direkcionog SFP modula SFP 1.25G TX 1550nm 10km DDM. SFP primopredajnici su visokih performansi, koji podržavaju dvostruku brzinu prenosa podataka od 1,25Gbps/1,0625Gbps i 20km udaljenosti prenosa sa SMF-om | Delivery and installation of the directional SFP module SFP 1.25G TX 1550nm 10km DDM. SFP transceivers are high-performance, supporting dual data rates of 1.25Gbps/1.0625Gbps and 20km transmission distance with SMF. | kom/pcs |  | 10 | 0
25. |  | Isporuka i montaža 24-portnog Fiber optic L2 switcha sličnog tipu H3C S5024FV3-EI. 24*100/1000Base-X SFP Portova, 2*10/100/1000Base-T Combo Porta i 4*1000Base-X Porta SFP | Delivery and installation of the 24-port Fiber optic L2 switch similar to the H3C S5024FV3-EI type. 24*100/1000Base-X SFP Ports, 2*10/100/1000Base-T Combo Ports and 4*1000Base-X SFP Ports. | kom/pcs |  | 1 | 0
26. |  | Isporuka i montaža upravljivog 24 portnog L2 PoE switcha sličnog tipu H3C S5024PV3-EI-HPWR. 24*10/100/1000Base-T PoE+ Ports(AC 370W,DC 740W) and 4*1000Base-X SFP Ports,(AC/DC) | Delivery and installation of a controllable 24-port L2 PoE switch similar to the type H3C S5024PV3-EI-HPWR. 24*10/100/1000Base-T PoE+ Ports (AC 370W, DC 740W) and 4*1000Base-X SFP Ports, (AC/DC) | kom/pcs |  | 7 | 0
27. |  | Isporuka i montaža upravljivog 24 portnog L2 switcha sličnog tipu H3C S5024PV3-E. 24*10/100/1000Base-T PoE+ Ports(AC 370W,DC 740W) and 4*1000Base-X SFP Ports,(AC/DC) | Delivery and installation of a controllable 24-port L2 switch similar to the H3C S5024PV3-E type. 24*10/100/1000Base-T PoE+ Ports (AC 370W, DC 740W) and 4*1000Base-X SFP Ports, (AC/DC). | kom/pcs |  | 13 | 0
28. |  | Isporuka i montaža Access Pointa za plafonsku montažu sličnog tipu H3C WA530. Dual band 802.11ac/n AP, velikog dometa. Dva 10/100/1000Mbps Ethernet porta (jedan od dva rada na PoE+) Mrežni portovi podržavaju agregaciju linkova (LACP) za redundantnost i povećan kapacitet. Jedan port za konzolu. Jedan USB port. 2.4GHz: 18dBm, 5GHz: 23dBm | Delivery and installation of the Access Point for ceiling mounting similar to the H3C WA530 type. Dual-band 802.11ac/n AP, long range. Two 10/100/1000Mbps Ethernet ports (one of two working on PoE+) Network ports support link aggregation (LACP) for redundancy and increased capacity. One console port. One USB port. 2.4GHz: 18dBm, 5GHz: 23dBm. | kom/pcs |  | 47 | 0
29. |  | Nabavka, isporuka i ugradnja muškog RJ-45 cat. 6 konektora. Ukupno za materijal i rad: | Supply, delivery and installation of male RJ-45 cat. 6 connectors. Total for material and works: | kom/pcs |  | 47 | 0
30. |  | Nabavka, isporuka i ugradnja telekomunikacionog jednomodularnog RJ-45 cat.6 modula u kompletu sa maskom u podnoj kutiji specificiranoj u projektu jake struje. Moduli su proizvođača SCHRACK ili slični, a ugrađuju se u modularne kutije proizvođača Ave, Legrand Mosaic ili sličnom. U cijenu je uračunato ispitivanje i izdavanje mjernih protokola. Ukupno za materijal i rad: | Supply, delivery and installation of telecommunications single-module RJ-45 cat.6 modules complete with mask in the floor box specified in the high voltage design. The modules are manufactured by SCHRACK or similar, and are installed in modular boxes manufactured by Ave, Legrand Mosaic or similar. The price includes examination and issuance of measurement protocols. Total for material and works: | kom/pcs |  | 132 | 0
31. |  | Nabavka, isporuka i ugradnja telekomunikacionog jednomodularnog RJ-45 cat.6 modula u kompletu sa maskom u odgovarajućim modularnim setovima iz predmjera jake i slabe struje, kao što je dato u prilozima projekta. Moduli su proizvođača SCHRACK ili slični, a ugrađuju se u modularne kutije proizvođača Ave, Legrand Mosaic ili sličnom. U cijenu je uračunato ispitivanje i izdavanje mjernih protokola. Ukupno za materijal i rad: | Procurement, delivery and installation of telecommunications single-modular RJ-45 cat.6 modules complete with mask inappropriate modular sets according to the Design of High and Low voltage installation, the attachments: Bill of Quantity. The modules are manufactured by SCHRACK or similar, and are installed in modular boxes manufactured by Ave, Legrand Mosaic or similar. The price includes examination and issuance of measurement protocols. Total for material and works: | kom/pcs |  | 157 | 0
32. |  | Isporuka i montaza dodatne podne prikljucne kutije od 14 modula za prihvatanje opreme za interaktivnu tablu | Delivery and installation of the additional floor connection box from 14 modules for accepting interactive whiteboard equipment | kom/pcs |  | 29 | 0
33. |  | Nabavka, isporuka i polaganje FTP LSZH kablova cat. 6 FRNC testiran do 400MHz, sertifikati DELTA & 3P - 'Wall', 4 parice, pun presjek, krstasti element između parica, FRNC (omotač bez halogena, nezapaljiv i ne ispušta dim), DELTA / EU sertifikovan; ostali sertifikati ISO9001, ISO14001, RoHS. Kablovi se polažu u odgovarajućim instalacionim cijevima po zidu ispod maltera. Ukupno za materijal i rad: | Procurement, delivery and installation of FTP LSZH cables cat. 6 FRNC tested up to 400MHz, DELTA & 3P - 'Wall' certified, 4 pairs, solid cross-section, cross element between pairs, FRNC (halogen-free sheath, non-flammable and smoke-free), DELTA / EU certified; other certificates ISO9001, ISO14001, RoHS. The cables are routed in suitable installation pipes on the wall under the plaster. Total for material and works: | m1 |  | 23200 | 0
34. |  | Nabavka, isporuka i polaganje fiber DRAKA optičkog kabla sa 2 fiber optička vlakna SM 9/125 µm LSZH G.657 A za unutrašnju upotrebu i vezu RACK Kablovi se polažu u instalacionim cijevima dijelom po zidu ispod maltera, a dijelom kroz betonsku ploču. Ukupno za materijal i rad: | Procurement, delivery and installation of DRAKA fibre optic cable with 2 fibre optic fibres SM 9/125 µm LSZH G.657 A for internal use and RACK connection. Cables are routed in installation pipes, partly on the wall under the plaster and partly through the concrete slab. Total for material and works: | m1 |  | 420 | 0
35. |  | Nabavka, isporuka i polaganje instalacionih halogen free cijevi unutrašnjeg prečnika Ø13mm kroz koje se provlače FTP cat.6 i optički kablovi. Ukupno za materijal i rad: | Procurement, delivery and placing of installation halogen-free pipes with an internal diameter of Ø13mm, through which FTP cat.6 and optical cables are passed. Total for material and works: | m1 |  | 21500 | 0
36. |  | Završno ispitivanje mreznih veza, izdavanje atesta DATA skenerom | Final examination of network connections, issuance of certificates by DATA scanner. | kom/pcs |  | 1 | 0
37. |  | Završno ispitivanje optickih veza, izdavanje atesta. | Final testing of optical connections and issuance of certificates. | kom/pcs |  | 1 | 0
38. |  | Isporuka i polaganje HDMI kabla duzine 10m | Delivery and installation of a 10m long HDMI cable. | kom/pcs |  | 29 | 0
39. |  | Nabavka, isporuka UTP cat. 6 kabla sa završnim RJ-45 konektorima na obije strane, dužine 0.5m-3m. Kabl služi za povezivanje patch panela sa aktivnom opremom. Ukupno za materijal i rad: | Procurement and delivery of UTP cat. 6 cables with end RJ-45 connectors on both sides, length 0.5m-3m. The cable serves to connect the patch panel with active equipment. Total for material and works: | kom/pcs |  | 300 | 0
40. |  | Nabavka i isporuka optičkih patch kord kablova sa završnim konektorima na obije strane, dužine 0.5m-3m. Kabl služi za povezivanje switch panela sa aktivnom opremom. Ukupno za materijal i rad: | Procurement and delivery of optical patch cord cables with end connectors on both sides, length 0.5m-3m. The cable serves to connect the switch panel with the active equipment. Total for material and works: | kom/pcs |  | 10 | 0
41. |  | Nabavka, isporuka i provlačenje koaksijalnog kabla tipa RG-6/CU 75Ω. Kabal se provlači kroz instalacione cijevi unutrašnjeg prečnika Ø13mm dijelom po zidu ispod maltera, a dijelom kroz betonsku košuljicu od OSS ormara do antenskih TV/SAT priključnica. Obračun vršiti po dužnom metru. Ukupno za materijal i rad: | Procurement, delivery and routing of coaxial cable type RG-6/CU 75Ω. The cable is passed through installation pipes with an internal diameter of Ø13mm, partly along the wall under the plaster and partly through the cement screed from the OSS cabinet to the antenna TV/SAT sockets. The calculation should be done according to measures of installed cables. Total for material and works: | m1 |  | 300 | 0
42. |  | Nabavka, isporuka i ugradnja priključnica za TV/SAT 5-2400 MHz. Priključnice su proizvodnje Schrack, Ave ili slične drugog proizvodjača. Ukupno za materijal i rad: | Procurement, delivery and installation of TV/SAT 5-2400 MHz sockets. The connectors are manufactured by Schrack, Ava or similar by another manufacturer. Total for material and works: | kom/pcs |  | 4 | 0
43. |  | Sitan montažni i nespecificirani materijal: | Necessary assembly material and unspecified material: | pauš/LS |  | 1 | 0
44. |  | Završno ispitivanje instalacije i puštanje u rad od strane isporučioca opreme. Izdavanje odgovarajućih atesta, obuka korisnika, puštanje u ispravan rad. | Final inspection of the installation and commissioning by the equipment supplier. Issuance of appropriate certificates, user training, and commissioning. | pauš/LS |  | 1 | 0
II. |  | INSTALACIJA STRUKTURNO KABLOVSKOG SISTEMA (SKS) | INSTALLATION OF STRUCTURAL CABLE SYSTEM (SCS) |  |  | Ukupno/Total | 0
III. |  | INSTALACIJA SISTEMA PROTIVPROVALE | INSTALLATION OF ANTI-BURGLARY SYSTEM
45. |  | Nabavka, isporuka i ugradnja alarmne centrale. Alarmna centrala 192 zone, BUS tehnologija, 8 zona na ploči (16 sa ATZ), 8 particija, 5 PGM izlaza na ploci, funkcija kontrole pristupa, do 254 modula za proširenje, dolazi u metalnoj kutiji dimenzija 280x280x80mm. Centrala je tipa EVO192/PCB, proizvođača PARADOX ili drugog. Ukupno za materijal i rad: | Procurement, delivery and installation of the alarm control panel. The alarm control panel has 192 zones, BUS technology, 8 zones on the board (16 with ATZ), 8 partitions, 5 PGM outputs on the board, the access control function, up to 254 expansion modules in the metal box measuring 280x280x80mm. The control unit is EVO192/PCB type, manufactured by PARADOX or others. Total for material and works: | kom/pcs |  | 1 | 0
46. |  | Isporuka i montaza modula koji radi kao repeat-er modul za instalaciju alarma, u kompletu sa kutijom, trafoom I baterijom 7Ah, sličan tipu PS25 Paradox..Ukupno za materijal i rad: | Delivery and assembly of a module that works as a repeater module for alarm installation, complete with box, transformer and 7Ah battery, similar to the PS25 Paradox type.Total for material and works: | kom/pcs |  | 2 | 0
47. |  | Isporuka i montaza modula za omogucavanje komunikacije sa drugim sistemima Paradox BUS2SER B203Integration Module In-field firmware upgradeable via a CONV4USB and WinLoad Supports ASCII / C-BUS protocols 16 virtual inputs to trigger an action in the EVO control panel based on an event received from the peripheral system using ASCII or C-BUS protocol 30 virtual PGMs to trigger an action in the peripheral system using ASCII or CBUS protocol based on an event received from the EVO control panel USB port for PC connections Provides an interface between an EVO control panel and a third party peripheral system Assign to one or more partitions 2048 event buffer | Delivery and assembly of modules to enable communication with other systems Paradox BUS2SER B203Integration Module In-field firmware upgradeable by the CONV4USB and WinLoad Supports ASCII / C-BUS protocols 16 virtual inputs to trigger an action in the EVO control panel based on an event received from the peripheral system using ASCII or C-BUS protocol 30 virtual PGMs to trigger an action in the peripheral system using ASCII or CBUS protocol based on an event received from the EVO control panel USB port for PC connections Provides an interface between an EVO control panel and a third party peripheral system Assign to one or more partitions 2048 event buffer | kom/pcs |  | 1 | 0
48. |  | Isporuka i montaza tastature: TM70 Touchscreen tastatura, displej 7'' + SOL ( LICENCA ) 7'' Ekran elegantnog dizajna, izuzetno tanak, kolor ekran (800x400pix), intuitivan graficki meni, kontroliše do 8 PGM izlaza, ažuriranje firmvera putem mikro SD kartice, snažan napredni procesor, jedan zonski/temperaturni ulaz za povezivanje detektora ili spoljnog temperaturnog senzora TEMP07, nazidna montaža, u bijeloj boji. Isporucuje se sa aktiviranom ''SpotOn Alarm Locator'' i '' Floor Plans'' funkcijom. | Keyboard delivery and assembly: TM70 Touchscreen keyboard, display 7'' + SOL ( LICENSE ) 7'' Screen of elegant design, extremely thin, colour screen (800x400pix), intuitive graphic menu, controls up to 8 PGM outputs, a firmware update via micro SD card, powerful advanced processor, one zone/temperature input for connection of detector or external temperature sensor TEMP07, wall mounting, in white colour. It comes with SpotOn Alarm Locator, and Floor Plans enabled. | kom/pcs |  | 1 | 0
49. |  | Nabavka, isporuka i ugradnja adresabilnog detektora pokreta Adresabilni detektor pokreta, domet 7x6m, vidni ugao 360°, sličan tipu DG467proizvođača Paradox ili drugog. Ukupno za materijal i rad: | Procurement, delivery and installation of the Addressable motion detector, range 12m, viewing angle 110°, digital with the quad sensor element, similar to type DM60 by Paradox or others. Total for material and works: | kom/pcs |  | 42 | 0
50. |  | Nabavka, isporuka i ugradnja plafonskog senzora za detekciju loma stakla, 7 digitalnih filtera frekfencije, zaštita od EMI i RFI talasa, podesiva osjetljivost, antisabotažni prekidač, dva režima rada - adresabilni i konvencionalni sa relejem, sličan tipu DG457 proizvođača Paradox. Ukupno za materijal i rad: | Procurement, delivery and installation of the ceiling sensor for detecting glass breakage, 7 digital frequency filters, protection against EMI and RFI waves, adjustable sensitivity, anti-sabotage switch, two operating modes - addressable and conventional with relay, similar to type DG457 manufactured by Paradox. Total for material and works: | kom/pcs |  | 42 | 0
51. |  | Nabavka, isporuka i ugradnja modula za prosirenje ZX8 Modul za proširenje, 8 zona (16 sa ATZ), 1 PGM. Ukupno za materijal i rad: | Supply, delivery and installation of expansion modules ZX8 Module for extension, 8 zones (16 with ATZ), 1 PGM. Total for material and works: | kom/pcs |  | 1 | 0
52. |  | Nabavka, isporuka i ugradnja sirene za dojavu provale slična tipu SOLO IBS L Spoljna sirena 128 dB sa blicerom, antisabotažno zašticena, dvostruko kucište, servisni mod.u. Ukupno za materijal i rad: | Procurement, delivery and installation of the burglar alarm siren similar to the SOLO IBS L type. External siren 128 dB with flasher, anti-sabotage protected, double housing, service mod. u. Total for material and works: | kom/pcs |  | 4 | 0
53. |  | Nabavka, isporuka i ugradnja antivandal sirene za unutrašnju montažu. Ukupno za materijal i rad: | Procurement, delivery and installation of an anti-vandal siren for internal installation. Total for material and works: | kom/pcs |  | 14 | 0
54. |  | Nabavka, isporuka i ugradnja senzora za detekciju vode PAradox. Ukupno za materijal i rad: | Procurement, delivery and installation of Paradox water detection sensors. Total for material and works: | kom/pcs |  | 10 | 0
55. |  | Nabavka, isporuka i provlačenje beshalogenog J-H(St)H 3x2x0.6mm² kabla. Kabl se provlači kroz odgovarajuće instalacione cijevi dijelom po zidu ispod maltera, dijelom kroz betonsku ploču, a dijelom iznad spuštenog plafona i služi za povezivanje elemenata protivprovalnog sistema. Ukupno za materijal i rad: | Procurement, delivery and installation of halogen-free J-H(St)H 3x2x0.6mm² cable. The cable is passed through the corresponding installation pipes, partly along the wall under the plaster, partly through the concrete slab, and partly above the suspended ceiling and is used to connect the elements of the anti-burglary system. Total for material and works: | m1 |  | 2520 | 0
56. |  | Nabavka, isporuka i polaganje instalacionih PVC cijevi unutrašnjeg prečnika Ø13mm kroz koju se provlače J-H(St)H 3x2x0.6mm² kablovi za povezivanje elemenata protivprovalnog sistema. Instalaciona cijev se polaže dijelom po zidu ispod maltera, dijelom kroz betonsku ploču, a dijelom iznad spuštenog plafona. Ukupno za materijal i rad: | Procurement, delivery and routing of installation PVC pipes with an internal diameter of Ø13mm, through which J-H(St)H 3x2x0.6mm² cables are passed for connecting the elements of the anti-burglary system. The installation pipe is routed partly on the wall under the plaster, partly through the concrete slab, and partly above the suspended ceiling. Total for material and works: | m1 |  | 2100 | 0
57. |  | Sitan montažni i nespecificirani materijal. | Necessary assembly material and unspecified material. | pauš/LS |  | 1 | 0
58. |  | Puštanje sistema u rad, obuka korisnika. Obračun po poziciji: | System commissioning, and user training. Calculation by position: | pauš/LS |  | 1 | 0
59. |  | Izrada uputstava i obuka korisnika | Preparation of instructions and user training | pauš/LS |  | 1 | 0
60. |  | Izrada projekta izvedenog stanja | Preparation of the as-built design. | pauš/LS |  | 1 | 0
III. |  | INSTALACIJA SISTEMA PROTIVPROVALE | INSTALLATION OF ANTI-BURGLARY SYSTEM |  |  | Ukupno/Total | 0
IV. |  | INSTALACIJA SISTEMA VIDEO NADZORA | INSTALLATION OF VIDEO SURVEILLANCE SYSTEM
61. |  | Nabavka, isporuka i ugradnja servera za video nadzor . Samostojeći 64 kanalni NVR, podržava 8Mpx/5Mpx/4Mpx/3Mpx/1080p DVC IP kamere, 8 x HDD,RAID 0,1,5,6,10; quadpleks, H.264/H.265 kompresija, brzina snimanja 8Mpx, 5Mpx, 4Mpx, 3Mpx, 1080p@1600fps, RS485, 2 x HDMI 4K i VGA video izlaz, 2P, LAN, DHCP, DDNS, WEB server, mobile client, dual strea+B214m, napajanje 230 VAC. Server se montira u rack ormaru RACK.POD u podrumu. Sličan tipu DRN-7864RZ RAID, proizvođača DVC. Ukupno za materijal i rad: | Procurement, delivery and installation of a server for video surveillance. Indipendent 64 channel NVR, support 8Mpx/5Mpx/4Mpx/3Mpx/1080p DVC IP cameras, 8 x HDD, RAID 0,1,5,6,10; quadplex, H.264/H.265 compression, recording speed 8Mpx, 5Mpx, 4Mpx, 3Mpx, 1080p@1600fps, RS485, 2 x HDMI 4K and VGA video output, 2P, LAN, DHCP, DDNS, WEB server, mobile client, dual stream+B214m, power supply 230 VAC. The server is mounted in the RACK.POD rack cabinet in the basement. Similar to the DRN-7864RZ RAID type manufactured by DVC. Total for material and works: | kom/pcs |  | 1 | 0
62. |  | Nabavka, isporuka i ugradnja HDD medijuma za potrebe video nadzora HDD HDD 6TB Seagate Skyhawk SEAGATE HDD za video snimače Skyhawk Guardian Surveillance (3.5/6TB/SATA 6Gb/s/rpm 7200). HDD se montira u serveru iz prethodne pozicije Sličan tipu HDD 6TB Seagate Skyhawk SEAGATE HDD. Ukupno za materijal i rad: | Procurement, delivery and installation of HDD media for video monitoring HDD HDD 6TB Seagate Skyhawk SEAGATE HDD for video Skyhawk Guardian Surveillance recorders (3.5/6TB/SATA 6Gb/s/rpm 7200). The HDD is mounted on the server from the previous position. Similar to the type of HDD 6TB Seagate Skyhawk SEAGATE HDD. Total for material and works: | kom/pcs |  | 8 | 0
63. |  | Nabavka, isporuka i ugradnja servera za video nadzor . Standalone 32 channel NVR, supports DVC IP cameras, 4 x HDD, quadpleks, H.264/H.265 compression, recording speed 8Mpx, 5Mpx, 4Mpx, 3Mpx, 1080p@25fps per channel, RS485, HDMI 4K and VGA video output, export USB MS, P2P, LAN, DHCP, DDNS. Server se montira u rack ormaru RACK.POD u podrumu. Sličan tipu DRN-3284R, proizvođača DVC. Ukupno za materijal i rad: | Procurement, delivery and installation of the server for video surveillance. Standalone 32-channel NVR, supports DVC IP cameras, 4 x HDD, quadplex, H.264/H.265 compression, recording speed 8Mpx, 5Mpx, 4Mpx, 3Mpx, 1080p@25fps per channel, RS485, HDMI 4K and VGA video output, export USB MS, P2P, LAN, DHCP, DDNS. The server is mounted in the RACK. RACK.POD cabinet in the basement. Similar to type DRN-3284R, manufactured by DVC. Total for material and works. | kom/pcs |  | 1 | 0
64. |  | Nabavka, isporuka i ugradnja HDD medijuma za potrebe video nadzora HDD HDD 6TB Seagate Skyhawk SEAGATE HDD za video snimače Skyhawk Guardian Surveillance (3.5/6TB/SATA 6Gb/s/rpm 7200). HDD se montira u serveru iz prethodne pozicije Sličan tipu HDD 6TB Seagate Skyhawk SEAGATE HDD. Ukupno za materijal i rad: | Procurement, delivery and installation of HDD media for video monitoring HDD HDD 6TB Seagate Skyhawk SEAGATE HDD for video Skyhawk Guardian Surveillance recorders (3.5/6TB/SATA 6Gb/s/rpm 7200). The HDD is mounted on the server from the previous position. Similar to the type of HDD 6TB Seagate Skyhawk SEAGATE HDD. Total for material and works: | kom/pcs |  | 2 | 0
65. |  | Nabavka, isporuka, ugradnja i programiranje bulet kamere, Bullet IP video kamera, rezolucija 5Mpx/20fps, objektiv 3.3 - 12 mm motorizirani zoom, H.265, 2 x Array Black glass IR LED dometa 30-50 m, 12VDC/PoE, Onvif, videoanalitika, IP67 zaštita., u kompletu sa nosačem. Slična tipu DCN-BM5125N, proizvođača DVC. Ukupno za materijal i rad: | Procurement, delivery, installation and programming of the bullet camera, Bullet IP video camera, resolution 5Mpx/20fps, lens 3.3 - 12 mm motorized zoom, H.265, 2 x Array Black glass IR LED range 30-50 m, 12VDC/PoE, Onvif, video analytics, IP67 protection., complete with bracket. Similar to type DCN-BM5125N, manufactured by DVC. Total for material and works: | kom/pcs |  | 18 | 0
66. |  | Nabavka, isporuka, ugradnja i programiranje Turret IP video camera, resolution 5Mpx/25fps, lens 2.8 mm, H.265, 1 x Array IR LED range 20-30 m, True WDR 120dB, 12VDC/PoE, SD-card, audio in, microphone, CVBS out, Onvif, IP67, VCA + face recognition u kompletu sa razvodnom kutijom, slična tipu DCN-TF5283F, proizvođača DVC. Ukupno za materijal i rad: | Procurement, delivery, installation and programming of Turret IP video camera, resolution 5Mpx/25fps, lens 2.8 mm, H.265, 1 x Array IR LED range 20-30 m, True WDR 120dB, 12VDC/PoE, SD-card, audio in, microphone, CVBS out, Onvif, IP67, VCA + face recognition complete with junction box, similar to type DCN-TF5283F, manufactured by DVC. Total for material and works: | kom/pcs |  | 52 | 0
67. |  | Nabavka, isporuka i ugradnja Profesionalnog monitor, 27'' u kompletu sa zidnim nosačem. Ukupno za materijal i rad: | Procurement, delivery and installation of a Professional monitor, 27'' complete with wall bracket. Total for material and works: | kom/pcs |  | 1 | 0
68. |  | Isporuka i montaža rekabilnog UPS uređaja snage 1700 VA, sličan tipu SOCOMEC NPR-1700-RT UPS. 1700VA/1350W 230V 50/60Hz AVR, Sine wave, LCD, RJ45, 1xUSB, 1xRS232 | Delivery and installation of a 1700 VA rechargeable UPS device, similar to the SOCOMEC NPR-1700-RT UPS type. 1700VA/1350W 230V 50/60Hz AVR, Sine wave, LCD, RJ45, 1xUSB, 1xRS232 | kom/pcs |  | 1 | 0
69. |  | Nabavka, isporuka, ugradnja i povezivanje kabla za video nadzor tipa U/FTP - 300Mhz 4x2x23AWG, Cat.6 za unutrašnju montažu, sa spoljašnjim omotačem LSZH, standardi: ISO/IEC 11801 2nd, EN 50173-1, IEC 61156-5, EN 50575 ukupne težine od 48 kg/km, kvalitativno ekvivalentan tipu SCHRACK TECHNIK, HSEKF423HB. Ukupno za materijal i rad: | Supply, delivery, installation and connection of cable for video surveillance type U/FTP - 300Mhz 4x2x23AWG, Cat.6 for indoor installation, with outer jacket LSZH, standards: ISO/IEC 11801 2nd, EN 50173-1, IEC 61156-5, EN 50575 with a total weight of 48 kg/km, qualitatively equivalent to the SCHRACK TECHNIK type, HSEKF423HB. Total for material and works: | m1 |  | 2900 | 0
70. |  | Nabavka, isporuka i polaganje instalacionih halogen free cijevi unutrašnjeg prečnika Ø13mm kroz koju se provlače kablovi , slična tipu HFXP20, proizvođača Dietzel Univolt. Instalaciona cijev se polaže po zidu ispod maltera. Ukupno za materijal i rad: | Procurement, delivery and routing of installation halogen-free pipes with an internal diameter of Ø13mm, through which cables are passed, similar to type HFXP20, manufactured by Dietzel Univolt. The installation pipe is routed on the wall under the plaster. Total for material and works: | m1 |  | 2500 | 0
71. |  | Sitan montažni i nespecificirani materijal: | Necessary assembly material and unspecified material: | pauš/LS |  | 1 | 0
72. |  | Završno ispitivanje instalacije i puštanje u rad od strane isporučioca opreme. Izdavanje odgovarajućih atesta, obuka korisnika, puštanje u ispravan rad. | Final inspection of the installation and commissioning by the equipment supplier. Issuance of appropriate certificates, user training, and commissioning. | pauš/LS |  | 1 | 0
IV. |  | INSTALACIJA SISTEMA VIDEO NADZORA | INSTALLATION OF VIDEO SURVEILLANCE SYSTEM |  |  | Ukupno/Total | 0
V. |  | INSTALACIJA SISTEMA AUTOMATSKE DOJAVE POŽARA | INSTALLATION OF AUTOMATIC FIRE ALARM SYSTEM
73. |  | Nabavka, isporuka i ugradnja adresabilne centrale sa dvije petlje, analogno adresabilna centrala sa dvije adresabilne petlje (2 x 240 adresabilnih uređaja), proširiva do 8 petlji, LCD tastatura, maksimalno 240 uređaja u petlji, 240 zona, podržara Enea, Vega, Apollo detektore. Broj upravljačkih panela 14 (SmartLetUSee / LCD), izlaza za napajanje 1, instaliranih nadziranih izlaznih alarma 1, ugrađenih izlaza za aktiviranje komunikatora 1, ugrađenih nadziranih izlaza greške 1, ugrađenih nenadziranih alarmnih izlaza 1, ugrađenih nenadziranih izlaza greške 1, izlaz za žičanu sirenu 1, stepen bezbjednosti EN54-2/EN54-4, napajanje glavno 230 VAC, napajanje pomoćno - baterija 2 x 12 VDC, 17 Ah napajač baterija 27,6Vdc, 4A, dimenzija 480 x 470 x 135 mm, težine 8kg, slična tipu S-SmartLoop2080/G, proizvođača Inim. Ukupno za materijal i rad: | Procurement, delivery and installation of an addressable switchboard with two loops, analogue addressable switchboard with two addressable loops (2 x 240 addressable devices), expandable to 8 loops, LCD keyboard, maximum 240 devices in a loop, 240 zones, supports Enea, Vega, Apollo number of control panels 14 (SmartLetUSee / LCD), power outputs 1, installed supervised alarm outputs 1, built-in outputs for activation of communicators 1, built-in supervised fault outputs 1, built-in unattended alarm outputs 1, installed unattended fault outputs 1, output for wired siren 1, safety level EN54-2/EN54-4, primary power supply 230 VAC, auxiliary power supply - battery 2 x 12 VDC, 17 Ah battery charger 27.6Vdc, 4A, dimensions 480 x 470 x 135 mm, weight 8kg, similar type S-SmartLoop2080/G, manufacturer Inim Total for material and work: | kom/pcs |  | 1 | 0
74. |  | Nabavka, isporuka i ugradnja baterija snage 17Ah/12Vdc, za napajanje centrale u slučaju nestanka struje. Ukupno za materijal i rad: | Procurement, delivery and installation of 17Ah/12Vdc batteries for powering the central office in case of power failure. Total for material and works: | kom/pcs |  | 4 | 0
75. |  | Nabavka, isporuka, montaža i povezivanje Modul proširenja za SmartLoop centrale za dojavu požara, 2 adresabilne petlje sa po 240 adresa, sličan tipu S-SmartLoop/2L proizvođača Inim. Ukupno za materijal i rad: | Procurement, delivery, assembly and connection Expansion module for SmartLoop fire alarm control panels, 2 addressable loops with 240 addresses each, similar to type S-SmartLoop/2L manufactured by Inim. Total for material and works: | kom/pcs |  | 2 | 0
76. |  | Nabavka, isporuka i ugradnja analogno-adresabilnog optičkog detektora dima, sličan tipu INIM S-ED100, proizvođača Inim. Ukupno za materijal i rad: | Procurement, delivery and installation of an analogue-addressable optical smoke detector, similar to the INIM S-ED100 type manufactured by Inim. Total for material and works: | kom/pcs |  | 336 | 0
77. |  | Nabavka, isporuka i ugradnja analogno-adresabilnog optičkog detektora dima, montaža u fiskulturnoj Sali, sličan tipu INIM S-ED100, proizvođača Inim. Ukupno za materijal i rad: | Procurement, delivery and installation of an analogue-addressable optical smoke detector, installation in Sports Hall, similar to the INIM S-ED100 type manufactured by Inim. Total for material and works: | kom/pcs |  | 12 | 0
78. |  | Nabavka, isporuka i ugradnja analogno-adresabilnog termodiferencijalnog detektora, sličan tipu INIM S-ED200, proizvođača Inim. Ukupno za materijal i rad: | Procurement, delivery and installation of an analogue-addressable thermodifferential detector, similar to the INIM S-ED200 type manufactured by Inim. Total for material and works: | kom/pcs |  | 8 | 0
79. |  | Nabavka, isporuka i montaža podnožja detektora predviđeno za smještaj Inim adresabilnih detektora, sličan tipu S-EB0010, proizvođača Inim. Ukupno za materijal i rad: | Procurement, delivery and installation of the detector base designed to accommodate Inim addressable detectors, similar to type S-EB0010, manufactured by Inim. Total for material and works: | kom/pcs |  | 356 | 0
80. |  | Nabavka, isporuka i montaža plastične pločice za označavanje detektora. Ukupno za materijal i rad: | Procurement, delivery and installation of the plastic plates for marking of detectors. Total for material and works: | kom/pcs |  | 356 | 0
81. |  | Nabavka, isporuka i montaža paralelnog indikatora prorade automatskih javljača. Paralelni indikator aktiviranja protivpožarnog detektora, namijenjen za Inim detektore serije Iris i Enea; svjetlosna signalizacija, sličan tipu S-IL0010, proizvođača Inim. Ukupno za materijal i rad: | Procurement, delivery and installation of a parallel indicator of the operation of automatic tellers. Parallel fire detector activation indicator, intended for Inim detectors of the Iris and Enea series; light signalling, similar to type S-IL0010, manufactured by Inim. Total for material and works: | kom/pcs |  | 155 | 0
82. |  | Nabavka, isporuka i ugradnja analogno-adresabilnog ručnog javljača požara komplet sa kućištem sličan tipu S-EC0020, proizvođača Inim. Ukupno za materijal i rad: | Procurement, delivery and installation of an analogue-addressable manual fire alarm complete with housing similar to type S-EC0020, manufactured by Inim. Total for material and works: | kom/pcs |  | 17 | 0
83. |  | Nabavka, isporuka i ugradnja adresabilne sirene za dojavu požara za unutrašnju montažu, (ES0010RE)Adresabilna sirena napajana iz petlje, moguće i vanjsko napajanje; integriran izolator kratkog spoja; u termoplastičnom crvenom kućištu; zidna montaža; odabir 14 tonova putem EITK2000 ili putem centrale Previdia/SmartLoop; 101dB(A)@1m(ovisno o izabranom tonu); Moguća i vanjska montaža IP65; Inim protokol slična tipu S-ES2010RE, proiuzvođača Inim. Ukupno za materijal i rad: | Procurement, delivery and installation of an addressable fire alarm siren for internal installation (ES0010RE). Addressable siren powered from a loop, external power supply possible; integrated short-circuit isolator; in a thermoplastic red case; wall mounting; selection of 14 tones via EITK2000 or the Previdia/SmartLoop control panel; 101dB(A)@1m (depending on the selected tone); External mounting IP65 is also possible; Inim protocol similar to type S-ES2010RE, manufactured by Inim. Total for material and works: | kom/pcs |  | 22 | 0
84. |  | Nabavka, isporuka i ugradnja adresabilnog ulazno/izlaznog modula. Ulazno-izlazni modul, 4 ulaza , 4 relejna (beznaponska) izlaza, Inim protokol, ugrađen izolator, slična tipu S-EM344R, proizvođača Inim. Ukupno za materijal i rad: | Procurement, delivery and installation of addressable input/output module. Input-output module, 4 inputs, 4 relays (voltage-free) outputs, Inim protocol, built-in isolator, similar to type S-EM344R, manufactured by Inim. Total for material and works: | kom/pcs |  | 12 | 0
85. |  | Nabavka, isporuka i ugradnja komunikatora za generisanje rezervne linije i pozivne funkcije GSM/GPRS-a, 5 programabilnih terminala, u kompletu sa metalnim kućištem. Sličan tipu i-SmartLink/AG. Ukupno za materijal i rad: | Procurement, delivery and installation of a communicator for generating a backup line and GSM/GPRS calling function, 5 programmable terminals, complete with a metal case. Similar to the i-SmartLink/AG type. Total for material and works: | kom/pcs |  | 1 | 0
86. |  | Nabavka, isporuka, montaža protivpožarne zaptivne mase negorivosti 120 min. | Procurement, delivery, and installation of fireproof sealant fire resistance 120 min. | kg |  | 10 | 0
87. |  | Nabavka, isporuka i polaganje bezhalogenog kabla signalizacije požara tipa JH(St)H 2x2x0.8 mm sa šildom, a plaća se po dužnom metru položenog kabla, a polaže se u odgovarajućim instalacionim halogen free PVC cijevima dijelom po zidu ispod maltera, dijelom kroz gipsane zidove, dijelom po plafonu, a dijelom po kablovskim regalima. Ukupno za materijal i rad: | Procurement, delivery and laying of halogen-free fire alarm cable type JH(St)H 2x2x0.8 mm with shield, which is paid per meter of the installed cable. The cable is installed in the appropriate installation halogen-free PVC pipes, partly on the wall under the plaster, partly through plaster walls, partly on the ceiling, and partly on the cable racks. Total for material and works: | m1 |  | 3850 | 0
88. |  | Nabavka, isporuka i polaganje bezhalogenog kabla signalizacije tipa JH(St)H 2x2x0.8 mm FE 180/E90 sa šildom, a plaća se po dužnom metru položenog kabla, a polaže se u odgovarajućim instalacionim halogen free PVC cijevima dijelom po zidu ispod maltera, dijelom kroz gipsane zidove, dijelom po plafonu, a dijelom po kablovskim regalima, a služi za povezivanje centrale sa BMS ormarom. Ukupno za materijal i rad: | Procurement, delivery and installation of halogen-free signalling cable type JH(St)H 2x2x0.8 mm FE 180/E90 with the shield. Payment is per meter of installed cable. The cable is routed in suitable installation halogen-free PVC pipes, partly on the wall under the plaster, partly through the plaster walls, partly on the ceiling, and partly on the cable racks. It serves to connect the switchboard with the BMS cabinet. Total for material and works: | m1 |  | 200 | 0
89. |  | Nabavka, isporuka i polaganje instalacionih halogen free PVC cijevi unutrašnjeg prečnika Ø13mm kroz koje se provlače kablovi za detekciju požara. Ukupno za materijal i rad: | Procurement, delivery and placing of installation halogen-free PVC pipes with the internal diameter of Ø13mm, through which cables for fire detection are installed. Total for material and works: | m1 |  | 2800 | 0
90. |  | Sitan montažni i nespecificirani materijal. | Necessary assembly material and unspecified material: | pauš/LS |  | 1 | 0
91. |  | Programiranje sistema dojave požara | Fire alarm system programming | pauš/LS |  | 1 | 0
92. |  | Puštanje sistema u rad, obuka korisnika, isporuka atesta o funkcionalnom ispitivanju. | Commissioning of the system, training of users, delivery of certificates of functional testing | pauš/LS |  | 1 | 0
93. |  | Izrada i isporuka projekta izvedenog stanja u el. Formi | Preparation and delivery of the as-built design in digital form | pauš/LS |  | 1 | 0
V. |  | INSTALACIJA SISTEMA AUTOMATSKE DOJAVE POŽARA | INSTALLATION OF AUTOMATIC FIRE ALARM SYSTEM |  |  | Ukupno/Total | 0
VI. |  | INSTALACIJA SISTEMA OZVUČENJA | SOUND SYSTEM INSTALLATION
94. |  | Nabavka, isporuka, montaža 4-zonskog mikrofona. Mikrofon se smješta u portirnicu i povezuje na 4-zonsko pojačalo preko RJ45 patch kablova koristeći SKS, sličan tipu Audac MPX48, proizvođača Audac. Ukupno za materijal i rad: | Procurement, delivery, and installation of the 4-zone microphone. The microphone is placed in the porter's room and connected to the 4-zone amplifier via the RJ45 patch cables using SKS, similar to the Audac MPX48 type manufactured by Audac. Total for material and works: | kom/pcs |  | 1 | 0
95. |  | Nabavka, isporuka i ugradnja 4-zonskog predpojačala, slično tipu Audac MTX48, proizvođača Audac. Ukupno za materijal i rad: | Procurement, delivery and installation of the 4-zone preamplifier, similar to the type Audac MTX48, manufactured by Audac. Total for material and works: | kom/pcs |  | 1 | 0
96. |  | Nabavka, isporuka, montaža izvora zvuka, digialni audio plejer CD, MP3 i FM tuner. sličan tipu Audac CMP30, proizvođača Audac. Ukupno za materijal i rad: | Procurement, delivery, and installation of sound sources, digital audio CD player, MP3 and FM tuner. Similar to the type Audac CMP30 manufactured by Audac. Total for material and works: | kom/pcs |  | 1 | 0
97. |  | Nabavka, isporuka, montaža i ugradnja pojačala snage 2x240W/100V, slično tipu Audac CAP224, proiuzvođača Audac. Ukupno za materijal i rad: | Procurement, delivery, assembly and installation of a power amplifier 2x240W/100V, similar to the type Audac CAP224, manufactured by Audac. Total for material and works: | kom/pcs |  | 1 | 0
98. |  | Nabavka, isporuka, montaža i ugradnja pojačala snage 4x240W/100V, slično tipu Audac CAP424, proiuzvođača Audac. Ukupno za materijal i rad: | Supply, delivery, assembly and installation of the power amplifier 4x240W/100V, similar to the type Audac CAP424, manufactured by Audac. Total for material and works: | kom/pcs |  | 1 | 0
99. |  | Nabavka, isporuka, montaža i ugradnja pojačala snage 4 x 120W, 100V., slično tipu Audac CAP424, proiuzvođača Audac. Ukupno za materijal i rad: | Procurement, delivery, assembly and installation of the power amplifier 4 x 120W, 100V., similar to the type Audac CAP424, manufactured by Audac. Total for material and works: | kom/pcs |  | 1 | 0
100. |  | Nabavka, isporuka, montaža i ugradnja atenuatora zvuka, slično tipu Audac VC3022/W, proiuzvođača Audac. Ukupno za materijal i rad: | Procurement, delivery, assembly and installation of a sound attenuator similar to the type Audac VC3022/W, manufactured by Audac. Total for material and works: | kom/pcs |  | 17 | 0
101. |  | Nabavka, isporuka, montaža i ugradnja atenuatora zvuka, slično tipu Audac VC3062/W, proiuzvođača Audac. Ukupno za materijal i rad: | Procurement, delivery, assembly and installation of the sound attenuator, similar to the type Audac VC3062/W, manufactured by Audac. Total for material and works: | kom/pcs |  | 3 | 0
102. |  | Nabavka, isporuka i montaža u modularni pribor 1M RCA audio priključnice. Ukupno za materijal i rad. Ukupno za materijal i rad: | Procurement, delivery and installation of 1M RCA audio jacks modular and accessories. Total for material and works: | kom/pcs |  | 2 | 0
103. |  | Nabavka, isporuka, montaža i ugradnja zvučnika snage 6W, sličan tipu Audac CIRA724/W., proiuzvođača Audac. Ukupno za materijal i rad: | Procurement, delivery, assembly and installation of 6W speakers, similar to the type Audac CIRA724/W., manufactured by Audac. Total for material and works: | kom/pcs |  | 167 | 0
104. |  | Nabavka, isporuka i provlačenje LiHCH 2x1.5mm kabla. Kabal se provlači kroz bezhalogene instalacione cijevi unutrašnjeg prečnika Ø13mm dijelom po zidu ispod maltera, a dijelom kroz podnu betonsku košuljicu, a služi za povezivanje elemenata sistema. Ukupno za materijal i rad: | Procurement, delivery and routing of LiHCH 2x1.5mm cable. The cable is passed through halogen-free installation pipes with the internal diameter of Ø13mm, partly along the wall under the plaster and partly through the concrete floor screed, and serves to connect the elements of the system. Total for material and works: | m1 |  | 2550 | 0
105. |  | Nabavka, isporuka i provlačenje LiHCH 4x1.5mm kabla. Kabal se provlači kroz bezhalogene instalacione cijevi unutrašnjeg prečnika Ø13mm dijelom po zidu ispod maltera, a dijelom kroz podnu betonsku košuljicu, a služi za povezivanje elemenata sistema. Ukupno za materijal i rad: | Procurement, delivery and routing of LiHCH 4x1.5mm cable. The cable is passed through halogen-free installation pipes with an internal diameter of Ø13mm, partly along the wall under the plaster and partly through the concrete floor liner, and serves to connect the elements of the system. Total for material and works: | m1 |  | 1350 | 0
106. |  | Nabavka, isporuka i polaganje instalacione halogen free cijevi unutrašnjeg prečnika Ø13mm, slična tipu HFXP20, proizvođača Deitzel Univolt. Instalaciona cijev se polaže dijelom po zidu ispod maltera, a dijelom kroz podnu betonsku košuljicu. Ukupno za materijal i rad: | Procurement, delivery and routing of installation halogen-free pipes with the internal diameter of Ø13mm, similar to type HFXP20, manufactured by Deitzel Univolt. The installation pipe is installed partly on the wall under the plaster and partly through the concrete floor screed. Total for material and works: | m1 |  | 350 | 0
107. |  | Nabavka, isporuka i priključivanje stereo kabla, dužine 1-1.5m, a koji služi za povezivanje aktivnih elemenata sistema u RACK ormaru. Ukupno za materijal i rad: | Procurement, delivery and connection of the stereo cable, 1-1.5m long, which is used to connect the active elements of the system in the RACK cabinet. Total for material and works: | kom/pcs |  | 5 | 0
108. |  | Nabavka, isporuka i priključivanje Cat6. patch kabla, dužine 2m, a koji služi za povezivanje 4-zonskog mikrofona u portirnici sa 4-zonskim predpojačalom u RACK ormaru preko SKS-a. Ukupno za materijal i rad: | Procurement, delivery and connection of Cat6. patch cable, 2m long, which is used to connect the 4-zone microphone in the door station with the 4-zone preamplifier in the RACK cabinet via SCS. Total for material and works: | kom/pcs |  | 2 | 0
109. |  | Sitan montažni i nespecificirani materijal. | Necessary assembly material and unspecified material: | pauš/LS |  | 1 | 0
110. |  | Potrebna merenja i ispitivanja na svim kablovskim trasama. | Necessary measurements and tests on all cable routes. | pauš/LS |  | 1 | 0
111. |  | Puštanje sistema u rad, obuka korisnika. Obračun po poziciji: | System commissioning, user training. Calculation by position: | pauš/LS |  | 1 | 0
VI. |  | INSTALACIJA SISTEMA OZVUČENJA | SOUND SYSTEM INSTALLATION |  |  | Ukupno/Total | 0
VII. |  | INSTALACIJA SISTEMA OZVUČENJA UČIONICE ZA MUZIČKO VASPITANJE | SOUND SYSTEM INSTALLATION OF THE CLASSROOM FOR MUSIC EDUCATION
|  | NAPOMENA: Predviđena pozicija pojačala je u RACK ormaru. | NOTE: The provided position of the amplifier is in the RACK cabinet.
112. |  | Nabavka isporuka i ugradnja AVR uredjaja slicnog tipu Sony STR-DH590 AV Receiver . Uredjaj se montira u stolu katedre a sluzi za povremeno pustanje muzickog sadrzaja. Ukupno za materijal i rad: | Procurement, delivery and installation of an AVR device similar to the Sony STR-DH590 type AV receiver. The device is mounted on the teacher's desk and used for occasional musical content playback. Total for material and works: | kom/pcs |  | 1 | 0
113. |  | Isporuka i montaza zvucnika slicnih tipu Klipsch CDT 3800 II in Ceiling Speaker . Zvucnici se montiraju u spustenom plafonu I povezuju direktno na AVR | Delivery and installation of speakers similar to the Klipsch CDT 3800 II in Ceiling Speaker type. The speakers are mounted in the suspended ceiling and connected directly to the AVR. | kom/pcs |  | 4 | 0
114. |  | Nabavka, isporuka i provlačenje LiHCH 2x1.5mm² kabla za zvučnike. Kabl se provlači kroz instalacione halogen free cijevi unutrašnjeg prečnika Ø13mm dijelom po zidu ispod maltera, dijelom iznad plafona, a dijelom po kablovskim regalima. Kabl se polaze od svakog zvucnika direktno u PPK kod katedre Ukupno za materijal i rad: | Procurement, delivery and routing of LiHCH 2x1.5mm² speaker cable. The cable is passed through the installation halogen-free tubes with the internal diameter of Ø13mm, partly along the wall under the plaster, partly above the ceiling, and partly along the cable racks. The cable routes from each speaker directly to the PPK at the teacher's desk.Total for material and works: | m1 |  | 100 | 0
115. |  | Nabavka, isporuka i polaganje halogen free instalacionih cijevi unutrašnjeg prečnika Ø13mm kroz koju se provlače kablovi tipa LiHCH 2x15mm² , slična tipu HFXP20, proizvođača Dietzel Univolt. Instalaciona cijev se polaže dijelom po zidu ispod maltera, a dijelom po plafonu. Ukupno za materijal i rad: | Procurement, delivery and routing of halogen-free installation pipes with the internal diameter of Ø13mm, through which cables of the LiHCH 2x15mm² type, similar to the HFXP20 type, manufactured by Dietzel Univolt, are passed. The installation pipe is routed partly on the wall under the plaster and partly on the ceiling. Total for material and works: | m1 |  | 100 | 0
116. |  | Sitan montažni i nespecificirani materijal. | Necessary assembly material and unspecified material: | pauš/LS |  | 1 | 0
117. |  | Puštanje sistema u rad, obuka korisnika. Obračun po poziciji: | System commissioning, user training. Calculation by position: | pauš/LS |  | 1 | 0
118. |  | Izrada uputstava i obuka korisnika: | Preparation of manuals and training of users. | pauš/LS |  | 1 | 0
119. |  | Izrada projekta izvedenog stanja u el. Formi | Preparation and delivery of the as-built design in digital form | pauš/LS |  | 1 | 0
VII. |  | INSTALACIJA SISTEMA OZVUČENJA UČIONICE ZA MUZIČKO VAS. | SOUND SYSTEM INSTALLATION OF THE CLASSROOM FOR MUSIC EDUCATION |  |  | Ukupno/Total | 0
VIII. |  | INSTALACIJA SISTEMA KONTROLE PRISTUPA | ACCESS CONTROL SYSTEM INSTALLATION
120. |  | Nabavka isporuka i ugradnja Kontrolera prolaza za do 4 vrata(4+4 opcionalni protokolarni čitači)Spider funkcionalnost ( može se koristiti kao RS-485/TCP/IP komunikacijksi konverter za dodatne kontrolere priključene na RS-485 komunikacijsku liniju), pamti do 30 000 događaja(proširivo na 100.000) i 100 000 događaja , dimenzije 222x222x80mm, TCP/IP i 2 x RS-485 komunikacija, ugrađeno napjanje 40W, AC230V, sličan tipu JAN POPULUS P-4-B, proizvođača Jantar. Ukupno za materijal i rad: | Procurement, delivery and installation of Gate Controllers for up to 4 doors (4+4 optional protocol readers), Spider functionality (can be used as an RS-485/TCP/IP communication converter for additional controllers connected to the RS-485 communication line), stores up to 30,000 events (expandable to 100,000) and 100,000 events, dimensions 222x222x80mm, TCP/IP and 2 x RS-485 communication, built-in voltage 40W, AC230V, similar to the type JAN POPULUS P-4-B, manufactured by Jantar. Total for material and works: | kom/pcs |  | 8 | 0
121. |  | Isporuka i montaza akumulatora 12v 7 ah | Delivery and installation of batteries 12v 7 ah | kom/pcs |  | 8 | 0
122. |  | Nabavka, isporuka i ugradnja Beskontaktnog čitač aJantar EM 125 kHz kartica, 3PRO Ready (Jantar protokol), IP65, očitanje do 7 cm, led i zvučna signalizacija, O tip kućišta. Povezivanje 4 žice. Moguće je povezivanje samo na kontrolere sa TCP/IP komunikacijom (Populus P-x-3P-NET i Trigger C-2-3PNET), sličan tipu JAN READER O-1-B, proiuzvođača jantar..Ukupno za materijal i rad: | Procurement, delivery and installation of the contactless reader Jantar EM 125 kHz card, 3PRO Ready (Jantar protocol), IP65, reading up to 7 cm, LED and sound signalling, O type housing. Connection 4 wires. It is possible to connect only to controllers with TCP/IP communication (Populus P-x-3P-NET and Trigger C-2-3PNET), similar to the type JAN READER O-1-B, manufactured by amber. Total for material and works: | kom/pcs |  | 16 | 0
123. |  | Nabavka, isporuka i ugradnja el.brave Electric strike, 12VDC Manufacturer: Assa Abloy, Eff Eff Uredjaj je slican tipu TSREK1705, proizvodjac SPICA. Ukupno za materijal i rad: | Procurement, delivery and installation of electric lock type Electric strike, 12VDC. Manufacturer: Assa Abloy, Eff Eff The device is similar to type TSREK1705, manufacturer SPICA. Total for material and works: | kom/pcs |  | 8 | 0
124. |  | Nabavka, isporuka i ugradnja magnetnog kontakta Ukupno za materijal i rad: | Supply, delivery and installation of magnetic contact. Total for material and works: | kom/pcs |  | 8 | 0
125. |  | Nabavka, isporuka i ugradnja Profesionalni klijentski računar. HP OMEN Tower, MB B450 (2xDDR4, M.2), AMD Ryzen 5 3600 (3.6 GHz, turbo bosst 4.2GHz), DDR4 16GB 3200 MHz, SSD 512GB M.2 NVMe, NVIDIA GeForce GTX 1660 SUPER 6GB, BLACK Ukupno za materijal i rad: | Procurement, delivery and installation of Professional client computer. HP OMEN Tower, MB B450 (2xDDR4, M.2), AMD Ryzen 5 3600 (3.6 GHz, turbo boost 4.2GHz), DDR4 16GB 3200 MHz, SSD 512GB M.2 NVMe, NVIDIA GeForce GTX 1660 SUPER 6GB, BLACK Total for material and work: | kom/pcs |  | 1 | 0
126. |  | Nabavka, isporuka i provlačenje KABLA LiHCH2x0.75 za bravu, mag.kontakt Kabl se provlači kroz instalacione halogen free cijevi unutrašnjeg prečnika Ø13mm dijelom po zidu ispod maltera, dijelom iznad plafona, a dijelom po kablovskim regalima. Ukupno za materijal i rad: | Procurement, delivery and routing of CABLE LiHCH2x0.75 for lock, magnetic contact. The cable is passed through the installation halogen-free pipes with the internal diameter of Ø13mm, partly along the wall under the plaster, partly above the ceiling, and partly along the cable racks. Total for material and works: | m1 |  | 200 | 0
127. |  | Nabavka, isporuka i polaganje FTP LSZH kablova cat. 6 FRNC testiran do 400MHz, sertifikati DELTA & 3P - 'Wall', 4 parice, pun presjek, krstasti element između parica, FRNC (omotač bez halogena, nezapaljiv i ne ispušta dim), DELTA / EU sertifikovan; ostali sertifikati ISO9001, ISO14001, RoHS. Kablovi se polažu u odgovarajućim instalacionim cijevima po zidu ispod maltera, a služe za vezu sa kontrolerom i čitačima kartica. Ukupno za materijal i rad: | Procurement, delivery and installation of FTP LSZH cables cat. 6 FRNC tested up to 400MHz, DELTA & 3P - 'Wall' certified, 4 pairs, solid cross-section, cross element between pairs, FRNC (halogen-free sheath, non-flammable and smoke-free), DELTA / EU certified; other certificates ISO9001, ISO14001, RoHS. The cables are routed in suitable installation pipes on the wall under the plaster, and are used for connection with the controller and card readers. Total for material and works: | m1 |  | 450 | 0
128. |  | Nabavka, isporuka i polaganje halogen free instalacionih cijevi unutrašnjeg prečnika Ø13mm kroz koju se provlače kablovi tipa LiHCH 2x15mm² , slična tipu HFXP20, proizvođača Dietzel Univolt. Instalaciona cijev se polaže dijelom po zidu ispod maltera, a dijelom po plafonu. Ukupno za materijal i rad: | Procurement, delivery and routing of halogen-free installation pipes with the internal diameter of Ø13mm, through which cables of the LiHCH 2x15mm² type, similar to the HFXP20 type, manufactured by Dietzel Univolt, are passed. The installation pipe is routed partly on the wall under the plaster and partly on the ceiling. Total for material and works: | m1 |  | 500 | 0
129. |  | Sitan montažni i nespecificirani materijal. | Necessary assembly material and unspecified material: | pauš/LS |  | 1 | 0
130. |  | Puštanje sistema u rad, obuka korisnika. Obračun po poziciji: | System commissioning, user training. Calculation by position: | pauš/LS |  | 1 | 0
131. |  | Izrada uputstava i obuka korisnika: | Preparation of manuals and training of users. | pauš/LS |  | 1 | 0
132. |  | Izrada projekta izvedenog stanja u el. Formi | Preparation and delivery of the as-built design in digital form | pauš/LS |  | 1 | 0
VIII. |  | INSTALACIJA SISTEMA KONTROLE PRISTUPA | ACCESS CONTROL SYSTEM INSTALLATION |  |  | Ukupno/Total | 0
IX. |  | INSTALACIJA SOS SISTEMA U TOALETIMA | SOS SYSTEM IN TOILETS INSTALLATION
133. |  | Nabavka, isporuka i ugradnja komplet razrešne kombinacije -tastera za poništenje alarma koji se postavlja u standardnu doznu fi 60 ili modularnu 2m. (pod stavkom se podrazumijevaju radovi štemanja za postavljanje kutije i fine obrade oko kutije nakon ugradnje) sličan tipu RK 2001, proizvodjača PME. Ukupno za materijal i rad: | Procurement, delivery and installation of the complete set of the solution combination - button for cancelling the alarm, installed in a standard fi 60 or modular 2m socket. the item includes the work of wall deepening and trimming for the installation of the box and fine processing around the box after installation) similar to the type RK 2001, manufactured by PME. Total for material and works: | kom/pcs |  | 2 | 0
134. |  | Nabavka, isporuka i ugradnja komplet signalne lampe sa zvučnim izvorom i napojnom jedinicom, koja se montira na ugradnu doznu fi78. (pod stavkom se podrazumijevaju radovi štemanja za postavljanje kutije i fine obrade oko kutije nakon ugradnje) slična tipu SSL+ZI+NJ, proizvodjača PME. Ukupno za materijal i rad: | Procurement, delivery and installation of the set of signal lamps with a sound source and the power supply unit, which is mounted on the fi78 built-in socket. (the itemincludes the work of wall deepening and trimming for the installation of the box and fine processing around the box after installation) similar to type SSL+ZI+NJ, manufactured by PME. Total for material and works: | kom/pcs |  | 2 | 0
135. |  | Nabavka, isporuka i ugradnja komplet alarmnog -pritisnog SOS tastera, koji se montira na zidu u og kutiji 80x80 ili u zidu u dozni fi60, pod stavkom se podrazumijevaju radovi štemanja za postavljanje kutije I fine obrade oko kutije nakon ugradnje) sličan tipu PK 2001, proizvodjača PME. Ukupno za materijal i rad: | Procurement, delivery and installation of a set of alarm-push SOS buttons, which is mounted on the wall in the box 80x80 or the box fi60; the item includes the work of wall deepening and trimming for the installation of the box and fine processing around the box after installation) similar to type PK 2001 of the PME manufacturer. Total for material and works: | kom/pcs |  | 2 | 0
136. |  | Nabavka, isporuka i polaganje kabla tipa JH(St)H 2x2x0,8 mm2 za povezivanje elemenata prema šemi veze koja je data u grafičkom prilogu (pod stavkom se podrazumijevaju radovi štemanja i fine obrade nakon polaganja kabla). Ukupno za materijal i rad: | Procurement, delivery and routing of cable type JH(St)H 2x2x0.8 mm2 for connecting elements according to the connection scheme in the graphic documentation (the item includes trimming and fine processing works after installation of the cable). Total for material and works: | m1 |  | 60 | 0
137. |  | Nabavka, isporuka i polaganje halogenfree instalacionih cijevi unutrašnjeg prečnika Ø13mm kroz koju se provlače kablovi. Instalaciona cijev se polaže dijelom po zidu ispod maltera, a dijelom kroz podnu betonsku košuljicu. Ukupno za materijal i rad: | Procurement, delivery and routing of halogen-free installation pipes with the internal diameter of Ø13mm, through which the cables are passed. The installation pipe is routed partly on the wall under the plaster and partly through the concrete floor screed. Total for material and works: | m1 |  | 40 | 0
138. |  | Povezivanje napojne jedinice koja je smještena u dozni iza signalne sirene sa razvodnom kutijom kablom tipa N2XH 3x2.5mm2 kao i povezivanje u razvodnoj kutiji. | Connection the power supply unit, located in the box behind the signal siren, with the junction box with the cable type N2XH 3x2.5mm2 and the link in the junction box. | kom/pcs |  | 2 | 0
139. |  | Sitni montažni i nespecificirani materijal. | Necessary assembly material and unspecified material: | pauš/LS |  | 1 | 0
140. |  | Povezivanje, programiranje i puštanje sistema u rad. | Connection, programming and commissioning the system. | pauš/LS |  | 1 | 0
IX. |  | INSTALACIJA SOS SISTEMA U TOALETIMA | SOS SYSTEM IN TOILETS INSTALLATION |  |  | Ukupno/Total | 0
X. |  | TELEFONSKA CENTRALA | TELEPHONE SWITCHBOARD
141. |  | Nabavka isporuka i ugradnja IP telefonske centrale hardverska Yeastar S50 Users: 50 Max Concurrent Calls: 25 Max Analog Ports: 8 Max BRI Ports: 8 Max Cellular Ports: 4 Max E1/T1/J1 Ports: N/A Expansion Board: N/A External Storage: SD Card Ukupno za materijal i rad: | Procurement, delivery and installation of IP PBX hardware unit Yeastar S50 Users: 50 Max Concurrent Calls: 25 Max Analog Ports: 8 Max BRI Ports: 8 Max Cellular Ports: 4 Max E1/T1/J1 Ports: N/A Expansion Board: N/ A External Storage: SD Card Total for material and works: | kom/pcs |  | 1 | 0
142. |  | Napredni IP telefon za direktora i sekretaricu Yealink SIP-T29G • Yealink Optima HD voice • Dual-port Gigabit Ethernet • 4.3" 480 x 272-pixel color display with backlight • Wi-Fi via WF40 • Bluetooth via BT40 • USB recording • Up to 16 SIP accounts • Paper label free design • PoE support • Headset, EHS support • Supports expansion modules • Stand with 2 adjustable angles • Wall mountable (optional) • Simple, flexible and secure provisioning options | Advanced IP phone for director and secretary Yealink SIP-T29G • Yealink Optima HD voice • Dual-port Gigabit Ethernet • 4.3"" 480 x 272-pixel color display with backlight • Wi-Fi via WF40 • Bluetooth via BT40 • USB recording • Up to 16 SIP accounts • Paper label-free design • PoE support • Headset, EHS support • Supports expansion modules • Stand with 2 adjustable angles • Wall mountable (optional) • Simple, flexible and secure provisioning options | kom/pcs |  | 2 | 0
143. |  | Nabavka isporuka i ugradnja telefona Yealink SIP-T31P• Yealink HD Voice• 2.3” 132x64-pixel graphical LCD with backlight• Two-port 10/100M Ethernet Switch• PoE support• Opus codec support• Up to 2 SIP accounts• Local 5-way conferencing• Support EHS Wireless Headset• Unified Firmware• Support YDMP/YMCS• Stand with 2 adjustable angles• Wall mountable Ukupno za materijal i rad: | Procurement, delivery and installation of telephone Yealink SIP-T31P• Yealink HD Voice• 2.3” 132x64-pixel graphical LCD with backlight• Two-port 10/100M Ethernet Switch• PoE support• Opus codec support• Up to 2 SIP accounts• Local 5-way conferencing• Support EHS Wireless Headset• Unified Firmware• Support YDMP/YMCS• Stand with 2 adjustable angles• Wall mountable. Total for material and works: | kom/pcs |  | 14 | 0
144. |  | Sitan montažni i nespecificirani materijal. | Necessary assembly material and unspecified material: | pauš/LS |  | 1 | 0
145. |  | Puštanje sistema u rad, obuka korisnika. Obračun po poziciji: | System commissioning, user training. Calculation by position: | pauš/LS |  | 1 | 0
146. |  | Izrada uputstava i obuka korisnika: | Preparation of manuals and training of users. | pauš/LS |  | 1 | 0
147. |  | Izrada projekta izvedenog stanja u el. Formi | Preparation and delivery of the as-built design in digital form | pauš/LS |  | 1 | 0
X. |  | TELEFONSKA CENTRALA | TELEPHONE SWITCHBOARD |  |  | Ukupno/Total | 0
XI. |  | KONTROLA ŠKOLSKOG ZVONA | SCHOOL BELL CONTROL
148. |  | Nabavka isporuka i ugradnja centralnog uredjaja za aktivaciju skolskog zvona. Uredjaj je Arcel communications ili slicanUkupno za materijal i | Procurement, delivery and installation of the central device for activating the school bell. The device is Arcel communications or similar. Total for material and work: | kom/pcs |  | 1 | 0
149. |  | Nabavka, isporuka i montaza tastera za rucnu aktivaciju skolskog zvona. Taster se uklapa u galanteriju jake struje a pozicija podrazumjeva doznu, nosac, masku i taster | Procurement, delivery and installation of the button for manual activation of the school bell. The button fits into the high-voltage accessories, and the position includes the dose, girder, mask and key | kom/pcs |  | 3 | 0
150. |  | Nabavka, isporuka i montaza skolskog zvona slicno tipu ELEKTRIČNO ŠKOLSKO ZVONO VEZ-10 | Procurement, delivery and installation of the school bell similar to the ELECTRIC SCHOOL BELL VEZ-10 type | kom/pcs |  | 3 | 0
151. |  | Nabavka, isporuka i polaganje kabla Ppy 3x1.5mm2 za povezivanje uredjaja iz pozicije 1 i tastera za rucnu aktivaciju sa zvonom | Procurement, delivery and installation of the PPY 3x1.5mm2 cable for connecting the device from position 1 and the button for manual activation with the bell | m1 |  | 100 | 0
152. |  | Montaža, povezivanje , konfiguracija i puštanje u rad kompletnog | Assembly, connection, configuration and commissioning of the complete system. | pauš/LS |  | 1 | 0
153. |  | Sitan montažni materijal | Necessary assembly material and unspecified material: | pauš/LS |  | 1 | 0
154. |  | Izrada projekta izvedenog stanja u el. Formi | Preparation and delivery of the as-built design in digital form | pauš/LS |  | 1 | 0
XI. |  | KONTROLA ŠKOLSKOG ZVONA | SCHOOL BELL CONTROL |  |  | Ukupno/Total | 0
XII. |  | NOSAČI KABLOVA | CABLE TRAYS
155. |  | Nabavka, isporuka i montaža perforiranih nosača kablova, sa brzom spojnicom, 60 x 300 x 3000 mm, napravljeni od pocinkovanog lima slični tipu RKSM E90 630 FS, proizvodjača OBO Bettermann. Stavka obuhvata nabavku, isporuku i ugradnju nosača, konzoli neophodnih za ugradnju nosača kablova. Ukupno za materijal i rad: | Supply, delivery and installation of perforated cable trays, with quick coupling, 60 x 300 x 3000 mm, made of galvanized sheet similar to type RKSM E90 630 FS, manufactured by OBO Bettermann. The item includes supplying, delivering, and installing girders and brackets necessary to install cable trays. Total for material and works: | kom/pcs |  | 3 | 0
156. |  | Nabavka, isporuka i montaža perforiranih nosača kablova, sa brzom spojnicom, 60 x 200 x 3000 mm, napravljeni od pocinkovanog lima slični tipu RKSM E90 620 FS, proizvodjača OBO Bettermann. Stavka obuhvata nabavku, isporuku i ugradnju nosača, konzoli neophodnih za ugradnju nosača kablova. Ukupno za materijal i rad: | Supply, delivery and installation of perforated cable trays, with quick coupling, 60 x 200 x 3000 mm, made of galvanized sheet similar to type RKSM E90 620 FS, manufactured by OBO Bettermann. The item includes supplying, delivering, and installing girders and brackets necessary to install cable trays. Total for material and works: | kom/pcs |  | 10 | 0
157. |  | Nabavka, isporuka i montaža T račve E90, horizontalna, sa Magic spojnicom, 60x300 mm, napravljena od pocinkovanog lima, proizvodjača OBO Bettermann. Ukupno za materijal i rad: | Supply, delivery and installation of T piece E90, horizontal, with Magic connector, 60x300 mm, made of galvanized sheet, manufactured by OBO Bettermann. Total for material and works: | kom/pcs |  | 1 | 0
158. |  | Nabavka, isporuka i montaža T račve E90, horizontalna, sa Magic spojnicom, 60x200 mm, napravljena od pocinkovanog lima, proizvodjača OBO Bettermann. Ukupno za materijal i rad: | Supply, delivery and installation of T piece E90, horizontal, with Magic connector, 60x200 mm, made of galvanized sheet, manufactured by OBO Bettermann. Total for material and works: | kom/pcs |  | 1 | 0
159. |  | Nabavka, isporuka i montaža krivine E90, horizontalna, sa Magic spojnicom, 60x300 mm, napravljena od pocinkovanog lima, proizvodjača OBO Bettermann. Ukupno za materijal i rad: | Supply, delivery and installation of arc E90, horizontal, with Magic connector, 60x300 mm, made of galvanized sheet, manufactured by OBO Bettermann. Total for material and works: | kom/pcs |  | 2 | 0
160. |  | Nabavka, isporuka i montaža krivine E90, horizontalna, sa Magic spojnicom, 60x200 mm, napravljena od pocinkovanog lima, proizvodjača OBO Bettermann. Ukupno za materijal i rad: | Supply, delivery and installation of arc E90, horizontal, with Magic connector, 60x200 mm, made of galvanized sheet, manufactured by OBO Bettermann. Total for material and works: | kom/pcs |  | 4 | 0
161. |  | Nabavka, isporuka i montaža perforiranih nosača kablova, sa brzom spojnicom, 60 x 300 x 3000 mm, napravljeni od pocinkovanog lima slični tipu MKS 630, proizvodjača OBO Bettermann. Stavka obuhvata nabavku, isporuku i ugradnju nosača, konzoli neophodnih za ugradnju nosača kablova. Ukupno za materijal i rad: | Supply, delivery and installation of perforated cable trays, with quick coupling, 60 x 300 x 3000 mm, made of galvanized sheet similar to type MKS 630, manufactured by OBO Bettermann. The item includes supplying, delivering, and installing girders and brackets necessary to install cable trays. Total for material and works: | kom/pcs |  | 70 | 0
162. |  | Nabavka, isporuka i montaža perforiranih nosača kablova, sa brzom spojnicom, 60 x 200 x 3000 mm, napravljeni od pocinkovanog lima slični tipu MKS 620, proizvodjača OBO Bettermann. Stavka obuhvata nabavku, isporuku i ugradnju nosača, konzoli neophodnih za ugradnju nosača kablova. Ukupno za materijal i rad: | Supply, delivery and installation of perforated cable trays, with quick coupling, 60 x 200 x 3000 mm, made of galvanized sheet similar to type MKS 620, manufactured by OBO Bettermann. The item includes supplying, delivering, and installing girders and brackets necessary to install cable trays. Total for material and works: | kom/pcs |  | 83 | 0
163. |  | Nabavka, isporuka i montaža perforiranih nosača kablova, sa brzom spojnicom, 60 x 100 x 3000 mm, napravljeni od pocinkovanog lima slični tipu MKS 610, proizvodjača OBO Bettermann. Stavka obuhvata nabavku, isporuku i ugradnju nosača, konzoli neophodnih za ugradnju nosača kablova. Ukupno za materijal i rad: | Supply, delivery and installation of perforated cable trays, with quick coupling, 60 x 100 x 3000 mm, made of galvanized sheet similar to type MKS 610, manufactured by OBO Bettermann. The item includes supplying, delivering, and installing girders and brackets necessary to install cable trays. Total for material and works: | kom/pcs |  | 69 | 0
164. |  | Nabavka, isporuka i montaža T račve, horizontalna, sa Magic spojnicom, 60x300 mm, napravljena od pocinkovanog lima, proizvodjača OBO Bettermann. Ukupno za materijal i rad: | Supply, delivery and installation of T piece, horizontal, with Magic connector, 60x300 mm, made of galvanized sheet, manufactured by OBO Bettermann. Total for material and work: | kom/pcs |  | 7 | 0
165. |  | Nabavka, isporuka i montaža T račve, horizontalna, sa Magic spojnicom, 60x200 mm, napravljena od pocinkovanog lima, proizvodjača OBO Bettermann. Ukupno za materijal i rad: | Supply, delivery and installation of T piece, horizontal, with Magic connector, 60x200 mm, made of galvanized sheet, manufactured by OBO Bettermann. Total for material and work: | kom/pcs |  | 8 | 0
166. |  | Nabavka, isporuka i montaža T račve, horizontalna, sa Magic spojnicom, 60x100 mm, napravljena od pocinkovanog lima, proizvodjača OBO Bettermann. Ukupno za materijal i rad: | Supply, delivery and installation of T piece, horizontal, with Magic connector, 60x100 mm, made of galvanized sheet, manufactured by OBO Bettermann. Total for material and work: | kom/pcs |  | 4 | 0
167. |  | Nabavka, isporuka i montaža krivine, horizontalna, sa Magic spojnicom, 60x300 mm, napravljena od pocinkovanog lima, proizvodjača OBO Bettermann. Ukupno za materijal i rad: | Supply, delivery and installation of arc, horizontal, with Magic connector, 60x300 mm, made of galvanized sheet, manufacturer OBO Bettermann. Total for material and work: | kom/pcs |  | 1 | 0
168. |  | Nabavka, isporuka i montaža krivine, horizontalna, sa Magic spojnicom, 60x200 mm, napravljena od pocinkovanog lima, proizvodjača OBO Bettermann. Ukupno za materijal i rad: | Supply, delivery and installation of arc, horizontal, with Magic connector, 60x200 mm, made of galvanized sheet, manufactured by OBO Bettermann. Total for material and works: | kom/pcs |  | 6 | 0
169. |  | Nabavka, isporuka i montaža krivine, horizontalna, sa Magic spojnicom, 60x100 mm, napravljena od pocinkovanog lima, proizvodjača OBO Bettermann. Ukupno za materijal i rad: | Supply, delivery and installation of arc, horizontal, with Magic connector, 60x100 mm, made of galvanized sheet, manufacturer OBO Bettermann. Total for material and works: | kom/pcs |  | 4 | 0
170. |  | Nabavka, isporuka i montaža usponskih lestvičastih nosača kablova, sa lučnom obujmicom i letvama, 50 x 300 x 3000 mm, napravljeni od pocinkovanog lima slični tipu SLL 360 NS proizvodjača OBO Bettermann. Ukupno za materijal i rad: | Supply, delivery and installation of riser ladder cable supports, with arc clamp and slats, 50 x 300 x 3000 mm, made of galvanized sheet similar to type SLL 360 NS by OBO Bettermann. Total for material and works: | kom/pcs |  | 4 | 0
171. |  | Sitan montažni i nespecificirani materijal (anker vijci, torban vijci, plasticni pokloci za zavrsetak nosaca I sl.). | Necessary assembly and unspecified material (anchor screws, bag screws, plastic covers for the end of the supports, etc.). | pauš/LS |  | 1 | 0
XII. |  | NOSAČI KABLOVA |  |  |  | Ukupno/Total | 0
3.2. |  | REKAPITULACIJA SLABA STRUJA | CABLE TRAYS
I. |  | GRAĐEVINSKI RADOVI | CIVIL WORKS |  |  |  | 0
II. |  | INSTALACIJA STRUKTURNO KABLOVSKOG SISTEMA (SKS) | INSTALLATION OF STRUCTURAL CABLE SYSTEM (SCS) |  |  |  | 0
III. |  | INSTALACIJA SISTEMA PROTIVPROVALE | INSTALLATION OF ANTI-BURGLARY SYSTEM |  |  |  | 0
IV. |  | INSTALACIJA SISTEMA VIDEO NADZORA | INSTALLATION OF VIDEO SURVEILLANCE SYSTEM |  |  |  | 0
V. |  | INSTALACIJA SISTEMA AUTOMATSKE DOJAVE POŽARA | INSTALLATION OF AUTOMATIC FIRE ALARM SYSTEM |  |  |  | 0
VI. |  | INSTALACIJA SISTEMA OZVUČENJA | SOUND SYSTEM INSTALLATION |  |  |  | 0
VII. |  | INSTALACIJA SISTEMA OZVUČENJA UČIONICE ZA MUZIČKO VAS. | SOUND SYSTEM INSTALLATION OF THE CLASSROOM FOR MUSIC EDUCATION |  |  |  | 0
VIII. |  | INSTALACIJA SISTEMA KONTROLE PRISTUPA | ACCESS CONTROL SYSTEM INSTALLATION |  |  |  | 0
IX. |  | INSTALACIJA SOS SISTEMA U TOALETIMA | SOS SYSTEM IN TOILETS INSTALLATION |  |  |  | 0
X. |  | TELEFONSKA CENTRALA | TELEPHONE SWITCHBOARD |  |  |  | 0
XI. |  | KONTROLA ŠKOLSKOG ZVONA | SCHOOL BELL CONTROL |  |  |  | 0
XII. |  | NOSAČI KABLOVA | CABLE TRAYS |  |  |  | 0
3.2. |  | UKUPNO SLABA STRUJA | TOTAL LOW VOLTAGE INSTALLATION |  |  |  | 0

## 3.3. BMS & EMP
Program obrazovanja Crne Gore / The education program of Montenegro
Predmjer - Izgradnja nove OŠ "Vladimir Nazor"/ Bill of Quantity - Construction of new Elementary School "Vladimir Nazor" BMS & EMP
br/No | predmet/ subject | NASLOV | NAME | mjerna jedinica/ UNIT | predt.cijena/ unit price in € | Količina/ Quantity | Cijena u eurima (bez PDV-a)/ Amount in € (without VAT)
(a) | (b) | (c) |  | ( d ) | (e) | (f) | (g=e*f)
3.3. |  | BMS I EMP | BMS AND EMP
|  | PREDMJER I PREDRAČUN BMS I EMP | BILL OF QUANTITY BMS AND EMP
I. |  | RAZVODNI ORMARI AUTOMATIKE | DISTRIBUTION CABINETS OF AUTOMATION
I a |  | Razvodni ormar ROA-TP | Distribution cabinet ROA-TP
1. |  | Razvodni orman izrađen od dva puta dekapiranog čeličnog lima debljine 2 mm sa bravicom i ključem u zaštiti IP-54. Ofarban i lakiran u boji po želji investitora. Ormar se postavlja na predvidjeno mijesto. Ulaz kablova je odozgo. Komplet urađen i montiran razvodni orman sa svim specificiranim i pomoćnim materijalom prema šemi delovanja, svi elementi vidno i trajno obiljeleženi. Jednopolna šema izvedenog ormana, plastificirana. Ormar približnih dimenzija 2000x2000x400 tip: 2xAT201042, ATSOB121--, ATSOC104--, ATSOT041-- Schrack Technik ili slično. | Distribution cabinet made of 2 mm thick steel sheet with lock and key in IP-54 protection. Painted and varnished in the colour desired by the investor. The cabinet is placed in place, provided by design. The cable entry is from above. Complete made and assembled distribution cabinet with all specified and auxiliary material according to the scheme of operation, all elements visibly and permanently marked. One-pole scheme of the manufactured cabinet plasticized. Cabinet of approximate dimensions 2000x2000x400 type: 2xAT201042, ATSOB121--, ATSOC104--, ATSOT041-- Schrack Technik or similar. | kom/ pcs |  | 1 | 0
2. |  | Glavni tropolni prekidač 80A, sa zaštitom od preoptertećenja 63-80A i zaštitom od kratkog spoja 480-800A, prekidne moći Icu=25kA, 415V, sa naponskim okidačem za napon 230V i za 50Hz sa pomocnim radnim kontaktom 6A, 230V. Tip: MC180131+MC199744+MM216380-- Schrack Technik ili slično. | Main three-pole switch 80A, with overload protection 63-80A and short-circuit protection 480-800A, breaking capacity Icu=25kA, 415V, with voltage release for voltage 230V and for 50Hz with auxiliary working contact 6A, 230V. Type: MC180131+MC199744+MM216380-- Schrack Technik or similar. | kom/ pcs |  | 1 | 0
3. |  | Taster za nužno isključenje ormara u slučaju havarije, pečurkasti, sa 2 radna kontakta za montažu na vrata, tip: MM216876+MM216374+MM216376... Sa dodatnim elementom za označavanje. Schrack Technik, ili slično. | Push button for the emergency shutdown of the cabinet, mushroom-shaped, with 2 working contacts for mounting on the door, type: MM216876+MM216374+MM216376. With additional marking elements. Schrack Technik, or similar. | kom/ pcs |  | 1 | 0
4. |  | Odvodnik prenapona (komplet) klase C 20kA 4p UAS20 280V, za montažu na šinu, sa pomoćnim kontaktima 1NO+1NC, 250VAC. Tip: IS010343 + IS010352---4k-- Schrack Technik ili slično. | Surge arrester (set) class C 20kA 4p UAS20 280V, for rail mounting, with auxiliary contacts 1NO+1NC, 250VAC. Type: IS010343 + IS010352-4k- Schrack Technik or similar. | kom/ pcs |  | 1 | 0
5. |  | Rele za kontrolu prisutnosti faza i asimetrije faza sa jednim preklopnim kontaktom NO/NC, 5A, 230V. Tip: UR5P3011-- Schrack Technik ili slično. | Relay for controlling the presence and asymmetry of phases with one switching contact NO/NC, 5A, 230V. Type: UR5P3011-- Schrack Technik or similar. | kom/ pcs |  | 1 | 0
6. |  | Ventilator sa fiterom za ormar, 19W, IP54. Tip: IUKNF2523A + IUKNE250 Schrack Technik ili slično. | Fan with fitter for the cabinet, 19W, IP54. Type: IUKNF2523A + IUKNE250 Schrack Technik or similar. | kom/ pcs |  | 1 | 0
7. |  | Termostat za ventilator za montažu na šinu, 1 N/O plavi. Tip: IUK08566-- Schrack Technik ili slično. | Rail Mount Fan Thermostat, 1 N/O Blue. Type: IUK08566-- Schrack Technik or similar. | kom/ pcs |  | 1 | 0
8. |  | Servisna svjetiljka 230V, 13W, 570mm sa mikroprekidačem. Tip: LID14409 Schrack Technik ili slično. | Service lamp 230V, 13W, 570mm with microswitch. Type: LID14409 Schrack Technik or similar. | kom/ pcs |  | 2 | 0
9. |  | Monofazna priključnica sa zaštitnim kontaktom 230V, 16A, za montažu na DIN šinu. Tip. BZ325000-A Schrack Technik ili slično. | Single-phase socket with protective contact 230V, 16A, for mounting on the DIN rail. Type. BZ325000-A Schrack Technik or similar. | kom/ pcs |  | 1 | 0
10. |  | UPS NeTYS PE 850VA/480W, 230V, 50/60Hz, AVR, RJ45, USB, Line interactive, Step wave. tip:NeTYS PE 850VA/480W, Socomec ili slično | UPS NeTYS PE 850VA/480W, 230V, 50/60Hz, AVR, RJ45, USB, Line interactive, Step wave. type: NeTYS PE 850VA/480W, Socomec or similar | kom/ pcs |  | 1 | 0
11. |  | Transformator za komandni napon, 230/24V, 50Hz, nazivne snage 400VA. Tip: LP602040T Schrack Technik ili slično. | Transformer for command voltage, 230/24V, 50Hz, rated power 400VA. Type: LP602040T Schrack Technik or similar. | kom/ pcs |  | 1 | 0
12. |  | Elektronsko napajanje 230VAC/24VDC, 10A, kućište za montažu na DIN šinu. Mean Well ili slično. | Electronic power supply 230VAC/24VDC, 10A, housing for mounting on a DIN rail. | kom/ pcs |  | 1 | 0
13. |  | Taster crni, 1NO. Tip MM216590+MM216374+MM216376, Schrack Technik ili slično. | Mean Well or something. | kom/ pcs |  | 1 | 0
14. |  | Motorna zastitna sklopka 1,60-2,50 sa 4 pomocna kontakta tip: BE502500+BE082882+BE072896--, Schrack Technik, ili slično | Button black, 1NO. Type MM216590+MM216374+MM216376, Schrack Technik or similar. | kom/ pcs |  | 3 | 0
15. |  | Motorna zastitna sklopka 6,30-10,00 sa 4 pomocna kontakta tip: BE510000+BE082882+BE072896--, Schrack Technik, ili slično | Motor protection switch 1.60-2.50 with 4 auxiliary contacts type: BE502500+BE082882+BE072896--, Schrack Technik, or similar | kom/ pcs |  | 1 | 0
16. |  | Motorna zastitna sklopka 10,00-16,00 sa 4 pomocna kontakta tip: BE516000+BE082882+BE072896--, Schrack Technik, ili slično | Motor protection switch 6.30-10.00 with 4 auxiliary contacts type: BE510000+BE082882+BE072896--, Schrack Technik, or similar | kom/ pcs |  | 2 | 0
17. |  | Tropolni motorni kontaktor 15kW, 32A, 400V, 50Hz, za komandni napon 230V, 50Hz sa 2 mirna i 3 radna pomoćna kontakta, tip: LTD13213+LTZ0D222, Schrack Technik, ili slično | Motor protection switch 10.00-16.00 with 4 auxiliary contacts type: BE516000+BE082882+BE072896--, Schrack Technik, or similar | kom/ pcs |  | 2 | 0
18. |  | Dvopolni grebenasti prekidač 1-0-2, za 20A, 400V, za montažu na vrata. Tip: IN006220-- Schrack Technik ili slično. | Two-pole cam switch 1-0-2, for 20A, 400V, for door mounting. Type: IN006220-- Schrack Technik or similar. | kom/ pcs |  | 8 | 0
19. |  | Pomoćno rele, sa 4 preklopna kontakta, za komandni napon 230VAC, 50Hz, sa odgovarajući, podnožjem. Tip: PT570730+YPT78704, Schrack Technik ili slično. | Auxiliary relay, with 4 switching contacts, for command voltage 230VAC, 50Hz, with the appropriate base. Type: PT570730+YPT78704, Schrack Technik or similar. | kom/ pcs |  | 19 | 0
20. |  | Pomoćno rele, sa 2 preklopna kontakta, za komandni napon 24VAC, 50Hz, sa odgovarajući, podnožjem. Tip: RT424524+ YRT78626, Schrack Technik ili slično. | Auxiliary relay, with 2 switching contacts, for command voltage 24VAC, 50Hz, with the appropriate base. Type: RT424524+ YRT78626, Schrack Technik or similar. | kom/ pcs |  | 16 | 0
21. |  | Pomoćno rele, sa 2 preklopna kontakta, za komandni napon 230VAC, 50Hz, sa odgovarajući, podnožjem. Tip: RT424730+ YRT78626, Schrack Technik ili slično. | Auxiliary relay, with 2 switching contacts, for command voltage 230VAC, 50Hz, with the appropriate base. Type: RT424730+ YRT78626, Schrack Technik or similar. | kom/ pcs |  | 3 | 0
22. |  | Pomoćno rele, sa 2 preklopna kontakta, za komandni napon 230VAC, 50Hz, sa odgovarajući, podnožjem. Tip: RT424730+ YRT78626, Schrack Technik ili slično. | Auxiliary relay, with 2 switching contacts, for command voltage 230VAC, 50Hz, with the appropriate base. Type: RT424730+ YRT78626, Schrack Technik or similar. | kom/ pcs |  | 6 | 0
23. |  | Jednopolni automatski instalacioni prekidač, 4A, sa termičkim i elektromagnetnim okidačem, 400V/230V, 10kA, k-ka C. Tip: BM617104, Schrack Technik ili slično. | Single-pole automatic installation switch, 4A, with the thermal and electromagnetic release, 400V/230V, 10kA, k-ka C. Type: BM617104, Schrack Technik or similar. | kom/ pcs |  | 3 | 0
24. |  | Jednopolni automatski instalacioni prekidač, 6A, sa termičkim i elektromagnetnim okidačem, 400V/230V, 10kA, k-ka C. Tip: BM617106, Schrack Technik ili slično. | Single pole automatic installation switch, 6A, with the thermal and electromagnetic release, 400V/230V, 10kA, k-ka C. Type: BM617106, Schrack Technik or similar. | kom/ pcs |  | 3 | 0
25. |  | Jednopolni automatski instalacioni prekidač, 10A, sa termičkim i elektromagnetnim okidačem, 400V/230V, 10kA, k-ka C. Tip: BM617110, Schrack Technik ili slično. | Single-pole automatic installation switch, 10A, with the thermal and electromagnetic release, 400V/230V, 10kA, k-ka C. Type: BM617110, Schrack Technik or similar. | kom/ pcs |  | 3 | 0
26. |  | Jednopolni automatski instalacioni prekidač,16A, sa termičkim i elektromagnetnim okidačem, 400V/230V, 10kA, k-ka C. Tip: BM617116, Schrack Technik ili slično. | Single-pole automatic installation switch, 16A, with the thermal and electromagnetic release, 400V/230V, 10kA, k-ka C. Type: BM617116, Schrack Technik or similar. | kom/ pcs |  | 3 | 0
27. |  | Jednopolni automatski instalacioni prekidač,25A, sa termičkim i elektromagnetnim okidačem, 400V/230V, 10kA, k-ka C. Tip: BM617125, Schrack Technik ili slično. | Single-pole automatic installation switch, 25A, with the thermal and electromagnetic release, 400V/230V, 10kA, k-ka C. Type: BM617125, Schrack Technik or similar. | kom/ pcs |  | 2 | 0
28. |  | Tropolni automatski instalacioni prekidač,4A, sa termičkim i elektromagnetnim okidačem, 400V/230V, 10kA, k-ka C. Tip: BM617304, Schrack Technik ili slično. | Three-pole automatic installation switch, 4A, with the thermal and electromagnetic release, 400V/230V, 10kA, k-ka C. Type: BM617304, Schrack Technik or similar. | kom/ pcs |  | 1 | 0
29. |  | Dvopolni automatski instalacioni osigurač DC-10A/C/2 pol 10KA, tip: BM015210, Schrack technik ili slično | Two-pole automatic installation fuse DC-10A/C/2 pole 10KA, type: BM015210, Schrack technik or similar | kom/ pcs |  | 1 | 0
30. |  | Signalna led dioda 230VAC, crvena Tip: BZ501215-B, Schrack Technik, ili slično. | Signal LED 230VAC, red Type: BZ501215-B, Schrack Technik, or similar. | kom/ pcs |  | 10 | 0
31. |  | Signalna led dioda 230VAC, zelena Tip: BZ501218-B, Schrack Technik, ili slično. | Signal LED 230VAC, green Type: BZ501218-B, Schrack Technik, or similar. | kom/ pcs |  | 10 | 0
32. |  | Signalna led dioda 230VAC, bijela Tip: BZ501219-B, Schrack Technik, ili slično. | Signal LED 230VAC, white Type: BZ501219-B, Schrack Technik, or similar. | kom/ pcs |  | 3 | 0
33. |  | Ethernet switch 8x10/100 Base -TX, 8xRJ45, neupravljivi za montažu na DIN šinu Napajanje: 12/24VDC, max 3,9W. (ŠxVxD) - 40mm x 114mm x 79mm Tip: SPIDER-SL-20-8T1999999SZ9HHHH proizvođač: Hirschmann ili slično | Ethernet switch 8x10/100 Base-TX, 8xRJ45, unmanageable for mounting on a DIN rail Power supply: 12/24VDC, max 3.9W. (WxHxD) - 40mm x 114mm x 79mm Type: SPIDER-SL-20-8T1999999SZ9HHHH manufacturer: Hirschmann or similar | kom/ pcs |  | 2 | 0
34. |  | Ethernet utičnica za montažu na din šinu Tip: proizvođač: Schrack Technik ili slično | Ethernet socket for din rail mounting Type: Manufacturer: Schrack Technik or similar | kom/ pcs |  | 4 | 0
35. |  | Nabavka, isporuka i montaža Metasys® Network Control Engine (NCE) 10 univerzalnih ulaza, 8 binarna ulaza, 4 analogna izlaza, 7 binarna izlaza, 4 konfigurabilna izlaza, 32-bitni mikroprocesor, Samoadaptivni PID. Sa FC Bus trunkom za integraciju BACnet MS/TP protokola. Sa BACnet IP komunikacijom za BMS. Sa integrisanim Web serverom. Sa opcijama za zadavanje vremenskih rasporeda, slanjem e-mail-a. Sa mogućnošću 3rd party integracije. BTL sertifikovan uređaj. Tip: MS-NCE2560-0 Proizvođač: Johnson Control ili slično. | Purchase, delivery and installation of Metasys® Network Control Engine (NCE) 10 universal inputs, 8 binary inputs, 4 analogue outputs, 7 binary outputs, 4 configurable outputs, 32-bit microprocessor, Self-adaptive PID. With FC Bus trunk for BACnet MS integration /TP protocol With BACnet IP communication for BMS With integrated Web server With options for setting time schedules, sending e-mail With the possibility of 3rd party integration BTL certified device. Type: MS-NCE2560-0 Manufacturer: Johnson Control or similar. | kom/ pcs |  | 1 | 0
36. |  | MS-FAC2611-0, Metasys Field Advanced Controller (FEC) Sat realnog vremena sa rasporedima, kalendarima, trendovima i alarmima Samoadaptivna PID regulacija. Napredna detekcija grešaka i prevencija. Komunikacija: BACnet MS/TP Ulazi/izlazi: 6UI, 2BI, 2AO, 3BO, 4CO Napajanje: 24 VAC Tip: MS-FAC2611-0 | MS-FAC2611-0, Metasys Field Advanced Controller (FEC) Real-time clock with schedules, calendars, trends and alarms Self-adaptive PID regulation. Advanced error detection and prevention. Communication: BACnet MS/TP Inputs/outputs: 6UI, 2BI, 2AO, 3BO, 4CO Power supply: 24 VAC Type: MS-FAC2611-0 | kom/ pcs |  | 1 | 0
37. |  | MS-IOM3721-0 Metasys ulazno/izlazni modul Komunikacija: BACnet MS/TP Ulazi/izlazi: 16BI Napajanje: 24 VAC Tip: MS-IOM3721-0 | MS-IOM3721-0 Metasys input/output module Communication: BACnet MS/TP Inputs/outputs: 16BI Power supply: 24 VAC Type: MS-IOM3721-0 | kom/ pcs |  | 1 | 0
38. |  | MS-IOM2721-0 Metasys ulazno/izlazni modul Komunikacija: BACnet MS/TP Ulazi/izlazi: 8UI, 2AO Napajanje: 24 VAC Tip: MS-IOM2721-0 | MS-IOM2721-0 Metasys input/output module Communication: BACnet MS/TP Inputs/outputs: 8UI, 2AO Power supply: 24 VAC Type: MS-IOM2721-0 | kom/ pcs |  | 8 | 0
39. |  | MS-IOM4711-0 Metasys ulazno/izlazni modul Komunikacija: BACnet MS/TP Ulazi/izlazi: Ulazi/izlazi: 6UI, 2BI, 2AO, 3BO, 4CO Napajanje: 24 VAC Tip: MS-IOM4711-0 | MS-IOM4711-0 Metasys input/output module Communication: BACnet MS/TP Inputs/outputs: Inputs/outputs: 6UI, 2BI, 2AO, 3BO, 4CO Power supply: 24 VAC Type: MS-IOM4711-0 | kom/ pcs |  | 1 | 0
40. |  | Touchscreen Advanced Display Slobodno programabilan interfejs TFT 64K boja, LED pozadinsko osvetljenje Komunikacija: BACnet MS/TP, BACnet IP Veličina: 7" , 480×272 px, 16:9 Napajanje: 24 VAC/DC, 300 mA Stepen zaštite: IP66 (IP20 nazad) Montaža na vrata el. ormana Masa : 0.6kg CE znak u skladu sa EMC i RoHS direktivama Tip: TAD0701-0 Proizvođač: Johnson Controls ili slično | Touchscreen Advanced Display Freely programmable interface TFT 64K colour, LED backlight Communication: BACnet MS/TP, BACnet IP Size: 7", 480×272 px, 16:9 Power supply: 24 VAC/DC, 300 mA Degree of protection: IP66 (IP20 back) Installation of the electric door wardrobe Weight: 0.6 kg CE mark in accordance with EMC and RoHS directives Type: TAD0701-0 Manufacturer: Johnson Controls or similar | kom/ pcs |  | 1 | 0
41. |  | Gateway, L-INX 202 2 x Ethernet: BACnet IP*, LIOB-IP, KNXnet, Modbus TCP 1 x LIOB-Connect 1 x LIOB-FT 1 x RS-485: BACnet MS/TP ili Modbus RTU * ili BACnet IP ili BACnet MS/TP Napajanje: 24VAC Sličan tipu: L-INX 202 Loytec ili slično | Gateway, L-INX 202 2 x Ethernet: BACnet IP*, LIOB-IP, KNXnet, Modbus TCP 1 x LIOB-Connect 1 x LIOB-FT 1 x RS-485: BACnet MS/TP or Modbus RTU * either BACnet IP or BACnet MS/TP Power supply: 24VAC Similar type: L-INX 202 Loytec or similar. | kom/ pcs |  | 5 | 0
42. |  | Sitan montažni materijal | Necessary assembly material | pauš/ LS |  | 1 | 0
43. |  | Šemiranje ormara | Planning of the cabinet according to installation schemes | pauš/ LS |  | 1 | 0
44. |  | Programiranje kontrolera i gateway-a ( 2 kontrolera i 5 gateway) | Controller and gateway programming (2 controllers and 5 gateways) | pauš/ LS |  | 1 | 0
45. |  | Programiranje HMI-a | HMI programming | pauš/ LS |  | 1 | 0
46. |  | Povezivanje ormara, podešavanje parametara automatike, funkcionalno ispitivanje i puštanje u rad. | Connection of cabinets, setting automation parameters, functional testing and commissioning. | pauš/ LS |  | 1 | 0
I a |  | RAZVODNI ORMAR ROA - TP | DISTRIBUTION CABINET ROA-TP |  |  | Ukupno | 0
I b |  | Razvodni ormar ROA-KK | Distribution cabinet ROA-KK
47. |  | Razvodni orman izrađen od dva puta dekapiranog čeličnog lima debljine 2 mm sa bravicom i ključem u zaštiti IP-54, 2 vrata. Ofarban i lakiran u boji po želji investitora. Ormar se postavlja na predvidjeno mijesto. Ulaz kablova je odozdo. Komplet urađen i montiran razvodni orman sa svim specificiranim i pomoćnim materijalom prema šemi delovanja, svi elementi vidno i trajno obiljeleženi. Jednopolna šema izvedenog ormana, plastificirana. Ormar približnih dimenzija 1400x1000x300 tip: WST1410302 + WSTWB006 +ASDRA400 Schrack Technik ili slično. | Distribution cabinet made of steel sheet 2 mm thick with lock and key in IP-54 protection, 2 doors. Painted and varnished in colour desired by the investor. The cabinet is placed in place according to design. The cable entry is from below. A set of completed and assembled switchboards with all specified and auxiliary materials according to the operation scheme, all elements visibly and permanently marked. Single-pole scheme of the built-in cabinet plasticized. Cabinet of approximate dimensions 1400x1000x300 type: WST1410302 + WSTWB006 +ASDRA400 Schrack Technik or similar. | kom/ pcs |  | 1 | 0
48. |  | Glavni tropolni prekidač 25A, sa zaštitom od preoptertećenja 20-25A i zaštitom od kratkog spoja 350A, prekidne moći Icu=25kA, 415V, sa naponskim okidačem za napon 230V i za 50Hz sa pomocnim radnim kontaktom 6A, 230V. Tip: MC125131+MC199744+MM216380-- Schrack Technik ili slično. | Main three-pole switch 25A, with overload protection 20-25A and short-circuit protection 350A, breaking capacity Icu=25kA, 415V, with voltage release for voltage 230V and for 50Hz with auxiliary working contact 6A, 230V. Type: MC125131+MC199744+MM216380-- Schrack Technik or similar. | kom/ pcs |  | 1 | 0
49. |  | Taster za nužno isključenje ormara u slučaju havarije, pečurkasti, sa 2 radna kontakta za montažu na vrata, tip: MM216876+MM216374+MM216376... Schrack Technik, ili slično. | Push-button for emergency shut-off of the cabinet, mushroom-shaped, with 2 working contacts for mounting on the door, type: MM216876+MM216374+MM216376. Schrack Technik, or similar. | kom/ pcs |  | 1 | 0
50. |  | Odvodnik prenapona (komplet) klase C 20kA 4p UAS20 280V, za montažu na šinu, sa pomoćnim kontaktima 1NO+1NC, 250VAC. Tip: IS010343 + IS010352---4k-- Schrack Technik ili slično. | Surge arrester (set) class C 20kA 4p UAS20 280V, for rail mounting, with auxiliary contacts 1NO+1NC, 250VAC. Type: IS010343 + IS010352-4k-Schrack Technik or similar. | kom/ pcs |  | 1 | 0
51. |  | Ventilator sa fiterom za ormar, 19W, IP54. Tip: IUKNF2523A + IUKNE250 Schrack Technik ili slično. | Fan with fitter for the cabinet, 19W, IP54. Type: IUKNF2523A + IUKNE250 Schrack Technik or similar. | kom/ pcs |  | 1 | 0
52. |  | Termostat za ventilator za montažu na šinu, 1 N/O plavi. Tip: IUK08566-- Schrack Technik ili slično. | Rail Mount Fan Thermostat, 1 N/O Blue. Type: IUK08566-- Schrack Technik or similar. | kom/ pcs |  | 1 | 0
53. |  | Servisna svjetiljka 230V, 13W, 570mm sa mikroprekidačem. Tip: LID14409 Schrack Technik ili slično. | Service lamp 230V, 13W, 570mm with microswitch. Type: LID14409 Schrack Technik or similar. | kom/ pcs |  | 1 | 0
54. |  | Monofazna priključnica sa zaštitnim kontaktom 230V, 16A, za montažu na DIN šinu. Tip. BZ325000-A Schrack Technik ili slično. | Single-phase socket with protective contact 230V, 16A, for mounting on a DIN rail. Type. BZ325000-A Schrack Technik or similar. | kom/ pcs |  | 1 | 0
55. |  | UPS NeTYS PE 650VA/360W, 230V, 50/60Hz, AVR, RJ45, USB, Line interactive, Step wave. tip:NeTYS PE 650VA/360W, Socomec ili slično | UPS NeTYS PE 650VA/360W, 230V, 50/60Hz, AVR, RJ45, USB, Line interactive, Step wave. type: NeTYS PE 650VA/360W, Socomec or similar | kom/ pcs |  | 1 | 0
56. |  | Transformator za komandni napon, 230/24V, 50Hz, nazivne snage 160VA. Tip: LP602016T Schrack Technik ili slično. | Transformer for command voltage, 230/24V, 50Hz, rated power 160VA. Type: LP602016T Schrack Technik or similar. | kom/ pcs |  | 1 | 0
57. |  | Vremenski rele za komandni napon 12-240V AC/DC sa 1 preklopnim kontaktom sa kašnjenjem pri uključenju/isključenju 0.1sec-10dana. Tip :ZR5ER011-- Schrack Technik ili slično. | Time relay for command voltage 12-240V AC/DC with 1 switching contact with on/off delay 0.1sec-10days. Type :ZR5ER011-- Schrack Technik or similar. | kom/ pcs |  | 1 | 0
58. |  | Taster crni, 1NC. Tip MM216590+MM216374+MM216378, Schrack Technik ili slično. | Button black, 1NC. Type MM216590+MM216374+MM216378, Schrack Technik or similar. | kom/ pcs |  | 2 | 0
59. |  | Taster crni, 1NO. Tip MM216590+MM216374+MM216376, Schrack Technik ili slično. | Button black, 1NO. Type MM216590+MM216374+MM216376, Schrack Technik or similar. | kom/ pcs |  | 1 | 0
60. |  | Motorna zastitna sklopka 6,30-10,00 sa 4 pomocna kontakta tip: BE510000+BE082882+BE072896--, Schrack Technik, ili slično | Motor protection switch 6.30-10.00 with 4 auxiliary contacts type: BE510000+BE082882+BE072896--, Schrack Technik, or similar. | kom/ pcs |  | 2 | 0
61. |  | Dvopolni grebenasti prekidač 1-0-2, za 20A, 400V, za montažu na vrata. Tip: IN006220-- Schrack Technik ili slično. | Two-pole cam switch 1-0-2, for 20A, 400V, for door mounting. Type: IN006220-- Schrack Technik or similar. | kom/ pcs |  | 2 | 0
62. |  | Pomoćno rele, sa 4 preklopna kontakta, za komandni napon 24VAC, 50Hz, sa odgovarajući, podnožjem. Tip: PT570524+YPT78704, Schrack Technik ili slično. | Auxiliary relay, with 4 switching contacts, for command voltage 24VAC, 50Hz, with the appropriate base. Type: PT570524+YPT78704, Schrack Technik or similar. | kom/ pcs |  | 1 | 0
63. |  | Pomoćno rele, sa 4 preklopna kontakta, za komandni napon 230VAC, 50Hz, sa odgovarajući, podnožjem. Tip: PT570730+YPT78704, Schrack Technik ili slično. | Auxiliary relay, with 4 switching contacts, for command voltage 230VAC, 50Hz, with the appropriate base. Type: PT570730+YPT78704, Schrack Technik or similar. | kom/ pcs |  | 8 | 0
64. |  | Pomoćno rele, sa 2 preklopna kontakta, za komandni napon 24VAC, 50Hz, sa odgovarajući, podnožjem. Tip: RT424524+ YRT78626, Schrack Technik ili slično. | Auxiliary relay, with 2 switching contacts, for command voltage 24VAC, 50Hz, with the appropriate base. Type: RT424524+ YRT78626, Schrack Technik or similar. | kom/ pcs |  | 16 | 0
65. |  | Pomoćno rele, sa 2 preklopna kontakta, za komandni napon 230VAC, 50Hz, sa odgovarajući, podnožjem. Tip: RT424730+ YRT78626, Schrack Technik ili slično. | Auxiliary relay, with 2 switching contacts, for command voltage 230VAC, 50Hz, with the appropriate base. Type: RT424730+ YRT78626, Schrack Technik or similar. | kom/ pcs |  | 2 | 0
66. |  | Jednopolni automatski instalacioni prekidač, 2A, sa termičkim i elektromagnetnim okidačem, 400V/230V, 10kA, k-ka C. Tip: BM617102, Schrack Technik ili slično. | Single-pole automatic installation switch, 2A, with the thermal and electromagnetic release, 400V/230V, 10kA, k-ka C. Type: BM617102, Schrack Technik or similar. | kom/ pcs |  | 5 | 0
67. |  | Jednopolni automatski instalacioni prekidač, 4A, sa termičkim i elektromagnetnim okidačem, 400V/230V, 10kA, k-ka C. Tip: BM617104, Schrack Technik ili slično. | Single-pole automatic installation switch, 4A, with the thermal and electromagnetic release, 400V/230V, 10kA, k-ka C. Type: BM617104, Schrack Technik or similar. | kom/ pcs |  | 3 | 0
68. |  | Jednopolni automatski instalacioni prekidač, 6A, sa termičkim i elektromagnetnim okidačem, 400V/230V, 10kA, k-ka C. Tip: BM617106, Schrack Technik ili slično. | Single pole automatic installation switch, 6A, with the thermal and electromagnetic release, 400V/230V, 10kA, k-ka C. Type: BM617106, Schrack Technik or similar. | kom/ pcs |  | 3 | 0
69. |  | Jednopolni automatski instalacioni prekidač, 10A, sa termičkim i elektromagnetnim okidačem, 400V/230V, 10kA, k-ka C. Tip: BM617110, Schrack Technik ili slično. | Single-pole automatic installation switch, 10A, with the thermal and electromagnetic release, 400V/230V, 10kA, k-ka C. Type: BM617110, Schrack Technik or similar. | kom/ pcs |  | 3 | 0
70. |  | Jednopolni automatski instalacioni prekidač,16A, sa termičkim i elektromagnetnim okidačem, 400V/230V, 10kA, k-ka C. Tip: BM617116, Schrack Technik ili slično. | Single-pole automatic installation switch, 16A, with the thermal and electromagnetic release, 400V/230V, 10kA, k-ka C. Type: BM617116, Schrack Technik or similar. | kom/ pcs |  | 1 | 0
71 |  | Signalna led dioda 230VAC, crvena Tip: BZ501215-B, Schrack Technik, ili slično. | Signal LED 230VAC, red Type: BZ501215-B, Schrack Technik, or similar. | kom/ pcs |  | 9 | 0
72. |  | Signalna led dioda 230VAC, zelena Tip: BZ501218-B, Schrack Technik, ili slično. | Signal LED 230VAC, green Type: BZ501218-B, Schrack Technik, or similar. | kom/ pcs |  | 2 | 0
73. |  | Signalna led dioda 230VAC, bijela Tip: BZ501219-B, Schrack Technik, ili slično. | Signal LED 230VAC, white Type: BZ501219-B, Schrack Technik, or similar. | kom/ pcs |  | 3 | 0
74. |  | Nabavka, isporuka i montaža Metasys® Network Control Engine (NCE) 10 univerzalnih ulaza, 8 binarna ulaza, 4 analogna izlaza, 7 binarna izlaza, 4 konfigurabilna izlaza, 32-bitni mikroprocesor, Samoadaptivni PID. Sa FC Bus trunkom za integraciju BACnet MS/TP protokola. Sa BACnet IP komunikacijom za BMS. Sa integrisanim Web serverom. Sa opcijama za zadavanje vremenskih rasporeda, slanjem e-mail-a. Sa mogućnošću 3rd party integracije. BTL sertifikovan uređaj. Tip: MS-NCE2560-0 Proizvođač: Johnson Control ili slično. | Supply, delivery and installation of Metasys® Network Control Engine (NCE) 10 universal inputs, 8 binary inputs, 4 analogue outputs, 7 binary outputs, 4 configurable outputs, 32-bit microprocessor, Self-adaptive PID. With FC Bus trunk for BACnet MS/TP protocol integration. With BACnet IP communication for BMS. With the integrated Web server. With options for setting time schedules by sending an e-mail. With the possibility of 3rd party integration. BTL-certified device. Type: MS-NCE2560-0 Manufacturer: Johnson Controls or similar. | kom/ pcs |  | 1 | 0
75. |  | MS-IOM3721-0 Metasys ulazno/izlazni modul Komunikacija: BACnet MS/TP Ulazi/izlazi: 16BI Napajanje: 24 VAC Tip: MS-IOM3721-0 | MS-IOM3721-0 Metasys input/output module Communication: BACnet MS/TP Inputs/outputs: 16BI Power supply: 24 VAC Type: MS-IOM3721-0 | kom/ pcs |  | 1 | 0
76. |  | MS-IOM2721-0 Metasys ulazno/izlazni modul Komunikacija: BACnet MS/TP Ulazi/izlazi: 8UI, 2AO Napajanje: 24 VAC Tip: MS-IOM2721-0 | MS-IOM2721-0 Metasys input/output module Communication: BACnet MS/TP Inputs/outputs: 8UI, 2AO Power supply: 24 VAC Type: MS-IOM2721-0 | kom/ pcs |  | 1 | 0
77. |  | MS-IOM4711-0 Metasys ulazno/izlazni modul Komunikacija: BACnet MS/TP Ulazi/izlazi: Ulazi/izlazi: 6UI, 2BI, 2AO, 3BO, 4CO Napajanje: 24 VAC Tip: MS-IOM4711-0 | MS-IOM4711-0 Metasys input/output module Communication: BACnet MS/TP Inputs/outputs: Inputs/outputs: 6UI, 2BI, 2AO, 3BO, 4CO Power supply: 24 VAC Type: MS-IOM4711-0 | kom/ pcs |  | 1 | 0
78. |  | Ethernet switch 5x10/100 Base -TX, 5xRJ45, neupravljivi za montažu na DIN šinu Napajanje: 12/24VDC, max 2,2W. (ŠxVxD) - 25mm x 114mm x 79mm Tip: SPIDER-SL-20-5T1999999SZ9HHHH proizvođač: Hirschmann ili slično | Ethernet switch 5x10/100 Base-TX, 5xRJ45, unmanageable for mounting on a DIN rail Power supply: 12/24VDC, max 2.2W. (WxHxD) - 25mm x 114mm x 79mm Type: SPIDER-SL-20-5T1999999SZ9HHHH Manufacturer: Hirschmann or similar | kom/ pcs |  | 1 | 0
79. |  | Ethernet utičnica za montažu na din šinu Tip: proizvođač: Schrack Technik ili slično | Ethernet socket for din rail mounting Type: Manufacturer: Schrack Technik or similar | kom/ pcs |  | 2 | 0
80. |  | Sitan montažni materijal | Necessary assembly material | pauš/LS |  | 1 | 0
81. |  | Šemiranje ormara | Planning of the cabinet according to installation schemes | pauš/LS |  | 1 | 0
82. |  | Programiranje kontrolera | Controller programming. | pauš/LS |  | 1 | 0
83. |  | Povezivanje ormara, podešavanje parametara automatike, funkcionalno ispitivanje i puštanje u rad. | Connecting cabinets, setting automation parameters, functional testing and commissioning. | pauš/LS |  | 1 | 0
I b |  | RAZVODNI ORMAR ROA - KK | DISTRIBUTION CABINET ROA - KK |  |  | Ukupno | 0
I c |  | RAZVODNI ORMAR ROA - VOD | DISTRIBUTION CABINET ROA - VOD
84. |  | Razvodni orman izrađen od dva puta dekapiranog čeličnog lima debljine 2 mm sa bravicom i ključem u zaštiti IP-54. Ofarban i lakiran u boji po želji investitora. Ormar se postavlja na predvidjeno mijesto. Ulaz kablova je odozgo. Komplet urađen i montiran razvodni orman sa svim specificiranim i pomoćnim materijalom prema šemi delovanja, svi elementi vidno i trajno obiljeleženi. Jednopolna šema izvedenog ormana, plastificirana. Ormar približnih dimenzija 2000x1600x400 tip: AT201642, ATSOB121--, ATSOC104--, ATSOT041-- Schrack Technik ili slično. | Distribution cabinet made of the steel sheet 2 mm thick with lock and key in IP-54 protection. Painted and varnished in the colour desired by the investor. The cabinet is placed in the place provided by design. The cable entry is from above. A set of completed and assembled switchboards with all specified and auxiliary materials according to the operation scheme, all elements visibly and permanently marked. Single-pole scheme of the built-in cabinet plasticized. Cabinet of approximate dimensions 2000x1600x400 type: AT201642, ATSOB121-, ATSOC104-, ATSOT041- Schrack Technik or similar. | kom/ pcs |  | 1 | 0
85. |  | Glavni tropolni prekidač 25A, sa zaštitom od preoptertećenja 20-25A i zaštitom od kratkog spoja 350A, prekidne moći Icu=25kA, 415V, sa naponskim okidačem za napon 230V i za 50Hz sa pomocnim radnim kontaktom 6A, 230V. Tip: MC125131+MC199744+MM216380-- Schrack Technik ili slično. | Main three-pole switch 25A, with overload protection 20-25A and short-circuit protection 350A, breaking capacity Icu=25kA, 415V, with voltage release for voltage 230V and for 50Hz with auxiliary working contact 6A, 230V. Type: MC125131+MC199744+MM216380- Schrack Technik or similar. | kom/ pcs |  | 1 | 0
86. |  | Taster za nužno isključenje ormara u slučaju havarije, pečurkasti, sa 2 radna kontakta za montažu na vrata, tip: MM216876+MM216374+MM216376... Schrack Technik, ili slično. | Push-button for emergency shut-off of the cabinet, mushroom-shaped, with 2 working contacts for mounting on the door, type: MM216876+MM216374+MM216376. Schrack Technik, or similar. | kom/ pcs |  | 1 | 0
87. |  | Odvodnik prenapona (komplet) klase C 20kA 4p UAS20 280V, za montažu na šinu, sa pomoćnim kontaktima 1NO+1NC, 250VAC. Tip: IS010343 + IS010352---4k-- Schrack Technik ili slično. | Surge arrester (set) class C 20kA 4p UAS20 280V, for rail mounting, with auxiliary contacts 1NO+1NC, 250VAC. Type: IS010343 + IS010352-4k-Schrack Technik or similar. | kom/ pcs |  | 1 | 0
88. |  | Rele za kontrolu prisutnosti faza i asimetrije faza sa jednim preklopnim kontaktom NO/NC, 5A, 230V. Tip: UR5P3011-- Schrack Technik ili slično. | Relay for controlling the presence and asymmetry of phases with one switching contact NO/NC, 5A, 230V. Type: UR5P3011-- Schrack Technik or similar. | kom/ pcs |  | 1 | 0
89. |  | Ventilator sa fiterom za ormar, 19W, IP54. Tip: IUKNF2523A + IUKNE250 Schrack Technik ili slično. | Fan with fitter for the cabinet, 19W, IP54. Type: IUKNF2523A + IUKNE250 Schrack Technik or similar. | kom/ pcs |  | 1 | 0
90. |  | Termostat za ventilator za montažu na šinu, 1 N/O plavi. Tip: IUK08566-- Schrack Technik ili slično. | Rail Mount Fan Thermostat, 1 N/O Blue. Type: IUK08566- Schrack Technik or similar. | kom/ pcs |  | 1 | 0
91. |  | Servisna svjetiljka 230V, 13W, 570mm sa mikroprekidačem. Tip: LID14409 Schrack Technik ili slično. | Service lamp 230V, 13W, 570mm with microswitch. Type: LID14409 Schrack Technik or similar. | kom/ pcs |  | 1 | 0
92. |  | Monofazna priključnica sa zaštitnim kontaktom 230V, 16A, za montažu na DIN šinu. Tip. BZ325000-A Schrack Technik ili slično. | Single-phase socket with protective contact 230V, 16A, for mounting on a DIN rail. Type. BZ325000-A Schrack Technik or similar. | kom/ pcs |  | 1 | 0
93. |  | UPS NeTYS PE 650VA/360W, 230V, 50/60Hz, AVR, RJ45, USB, Line interactive, Step wave. tip:NeTYS PE 650VA/360W, Socomec ili slično | UPS NeTYS PE 650VA/360W, 230V, 50/60Hz, AVR, RJ45, USB, Line interactive, Step wave. type: NeTYS PE 650VA/360W, Socomec or similar | kom/ pcs |  | 1 | 0
94. |  | Transformator za komandni napon, 230/24V, 50Hz, nazivne snage 160VA. Tip: LP602016T Schrack Technik ili slično. | Transformer for command voltage, 230/24V, 50Hz, rated power 160VA. Type: LP602016T Schrack Technik or similar. | kom/ pcs |  | 1 | 0
95. |  | Elektronsko napajanje 230VAC/24VDC, 5A 120W, kućište za montažu na DIN šinu. Tip: LP749120-- Schrack Technik ili slično. | Electronic power supply 230VAC/24VDC, 5A 120W, DIN rail mounting housing. Type: LP749120-- Schrack Technik or similar. | kom/ pcs |  | 1 | 0
96. |  | Vremenski rele za komandni napon 12-240V AC/DC sa 1 preklopnim kontaktom sa kašnjenjem pri uključenju/isključenju 0.1sec-10dana. Tip :ZR5ER011-- Schrack Technik ili slično. | Time relay for command voltage 12-240V AC/DC with 1 switching contact with on/off delay 0.1sec-10days. Type: ZR5ER011-- Schrack Technik or similar. | kom/ pcs |  | 1 | 0
97. |  | Taster crni, 1NC. Tip MM216590+MM216374+MM216378, Schrack Technik ili slično. | Button black, 1NC. Type MM216590+MM216374+MM216378, Schrack Technik or similar. | kom/ pcs |  | 2 | 0
98. |  | Taster crni, 1NO. Tip MM216590+MM216374+MM216376, Schrack Technik ili slično. | Button black, 1NO. Type MM216590+MM216374+MM216376, Schrack Technik or similar. | kom/ pcs |  | 1 | 0
99. |  | Motorna zastitna sklopka 0,63-1 sa 4 pomocna kontakta tip: BE501000+BE082882+BE072896--, Schrack Technik, ili slično | Motor protection switch 0.63-1 with 4 auxiliary contacts type: BE501000+BE082882+BE072896- Schrack Technik, or similar. | kom/ pcs |  | 2 | 0
100. |  | Motorna zastitna sklopka 1,60-2,50 sa 4 pomocna kontakta tip: BE502500+BE082882+BE072896--, Schrack Technik, ili slično | Motor protection switch 1.60-2.50 with 4 auxiliary contacts type: BE502500+BE082882+BE072896-, Schrack Technik, or similar | kom/ pcs |  | 6 | 0
101. |  | Motorna zastitna sklopka 4,00-6,30 sa 4 pomocna kontakta tip: BE506300+BE082882+BE072896--, Schrack Technik, ili slično | Motor protection switch 4.00-6.30 with 4 auxiliary contacts type: BE506300+BE082882+BE072896-, Schrack Technik, or similar | kom/ pcs |  | 2 | 0
102. |  | Tropolni motorni kontaktor 4kW, 9A, 400V, 50Hz, za komandni napon 230V, 50Hz sa 2 mirna i 3 radna pomoćna kontakta. tip: LTD00913+LTZ0D222, Schrack Technik ili slično. | Three-pole motor contactor 4kW, 9A, 400V, 50Hz, for command voltage 230V, 50Hz with 2 non-stop and 3 working auxiliary contacts. type: LTD00913+LTZ0D222, Schrack Technik or similar. | kom/ pcs |  | 16 | 0
103. |  | Dvopolni grebenasti prekidač 1-2-3-4, za 20A, 400V, za montažu na vrata, tip: IN003124-- Schrack Technik, ili slično | Two-pole cam switch 1-2-3-4, for 20A, 400V, for door mounting, type: IN003124-- Schrack Technik, or similar | kom/ pcs |  | 6 | 0
104. |  | Dvopolni grebenasti prekidač 1-2-3-4, za 20A, 400V, za montažu na vrata, tip: IN003124-- Schrack Technik, ili slično | Two-pole cam switch 1-2-3-4, for 20A, 400V, for door mounting, type: IN003124-- Schrack Technik, or similar | kom/ pcs |  | 5 | 0
105. |  | Pomoćno rele, sa 4 preklopna kontakta, za komandni napon 24VAC, 50Hz, sa odgovarajući, podnožjem. Tip: PT570524+YPT78704, Schrack Technik ili slično. | Auxiliary relay, with 4 switching contacts, for command voltage 24VAC, 50Hz, with the appropriate base. Type: PT570524+YPT78704, Schrack Technik or similar. | kom/ pcs |  | 4 | 0
106. |  | Pomoćno rele, sa 4 preklopna kontakta, za komandni napon 230VAC, 50Hz, sa odgovarajući, podnožjem. Tip: PT570730+YPT78704, Schrack Technik ili slično. | Auxiliary relay, with 4 switching contacts, for command voltage 230VAC, 50Hz, with the appropriate base. Type: PT570730+YPT78704, Schrack Technik or similar. | kom/ pcs |  | 10 | 0
107. |  | Pomoćno rele, sa 2 preklopna kontakta, za komandni napon 24VAC, 50Hz, sa odgovarajući, podnožjem. Tip: RT424524+ YRT78626, Schrack Technik ili slično. | Auxiliary relay, with 2 switching contacts, for command voltage 24VAC, 50Hz, with the appropriate base. Type: RT424524+ YRT78626, Schrack Technik or similar. | kom/ pcs |  | 18 | 0
108. |  | Pomoćno rele, sa 2 preklopna kontakta, za komandni napon 230VAC, 50Hz, sa odgovarajući, podnožjem. Tip: RT424730+ YRT78626, Schrack Technik ili slično. | Auxiliary relay, with 2 switching contacts, for command voltage 230VAC, 50Hz, with the appropriate base. Type: RT424730+ YRT78626, Schrack Technik or similar. | kom/ pcs |  | 3 | 0
109. |  | Jednopolni automatski instalacioni prekidač, 2A, sa termičkim i elektromagnetnim okidačem, 400V/230V, 10kA, k-ka C. Tip: BM617102, Schrack Technik ili slično. | Single-pole automatic installation switch, 2A, with the thermal and electromagnetic release, 400V/230V, 10kA, k-ka C. Type: BM617102, Schrack Technik or similar. | kom/ pcs |  | 7 | 0
110. |  | Jednopolni automatski instalacioni prekidač, 4A, sa termičkim i elektromagnetnim okidačem, 400V/230V, 10kA, k-ka C. Tip: BM617104, Schrack Technik ili slično. | Single-pole automatic installation switch, 4A, with the thermal and electromagnetic release, 400V/230V, 10kA, k-ka C. Type: BM617104, Schrack Technik or similar. | kom/ pcs |  | 3 | 0
111. |  | Jednopolni automatski instalacioni prekidač, 6A, sa termičkim i elektromagnetnim okidačem, 400V/230V, 10kA, k-ka C. Tip: BM617106, Schrack Technik ili slično. | Single pole automatic installation switch, 6A, with the thermal and electromagnetic release, 400V/230V, 10kA, k-ka C. Type: BM617106, Schrack Technik or similar. | kom/ pcs |  | 5 | 0
112. |  | Jednopolni automatski instalacioni prekidač, 10A, sa termičkim i elektromagnetnim okidačem, 400V/230V, 10kA, k-ka C. Tip: BM617110, Schrack Technik ili slično. | Single-pole automatic installation switch, 10A, with the thermal and electromagnetic release, 400V/230V, 10kA, k-ka C. Type: BM617110, Schrack Technik or similar. | kom/ pcs |  | 1 | 0
113. |  | Jednopolni automatski instalacioni prekidač,16A, sa termičkim i elektromagnetnim okidačem, 400V/230V, 10kA, k-ka C. Tip: BM617116, Schrack Technik ili slično. | Single-pole automatic installation switch, 16A, with the thermal and electromagnetic release, 400V/230V, 10kA, k-ka C. Type: BM617116, Schrack Technik or similar. | kom/ pcs |  | 1 | 0
114. |  | Tropolni automatski instalacioni prekidač,4A, sa termičkim i elektromagnetnim okidačem, 400V/230V, 10kA, k-ka C. Tip: BM617304, Schrack Technik ili slično. | Three-pole automatic installation switch, 4A, with the thermal and electromagnetic release, 400V/230V, 10kA, k-ka C. Type: BM617304, Schrack Technik or similar. | kom/ pcs |  | 1 | 0
115. |  | Tropolni automatski instalacioni prekidač,6A, sa termičkim i elektromagnetnim okidačem, 400V/230V, 10kA, k-ka C. Tip: BM617306, Schrack Technik ili slično. | Three-pole automatic installation switch, 6A, with the thermal and electromagnetic release, 400V/230V, 10kA, k-ka C. Type: BM617306, Schrack Technik or similar. | kom/ pcs |  | 1 | 0
116. |  | Dvopolni automatski instalacioni osigurač DC-6A/C/2 pol 10KA, tip: BM015206, Schrack technik ili slično | Double pole automatic installation fuse DC-6A/C/2 pole 10KA, type: BM015206, Schrack technik or similar | kom/ pcs |  | 1 | 0
117. |  | Signalna led dioda 230VAC, crvena Tip: BZ501215-B, Schrack Technik, ili slično. | Signal LED 230VAC, red Type: BZ501215-B, Schrack Technik, or similar. | kom/ pcs |  | 12 | 0
118. |  | Signalna led dioda 230VAC, zelena Tip: BZ501218-B, Schrack Technik, ili slično. | Signal LED 230VAC, green Type: BZ501218-B, Schrack Technik, or similar. | kom/ pcs |  | 13 | 0
119. |  | Signalna led dioda 230VAC, bijela Tip: BZ501219-B, Schrack Technik, ili slično. | Signal LED 230VAC, white Type: BZ501219-B, Schrack Technik, or similar. | kom/ pcs |  | 3 | 0
120 |  | Ethernet switch 5x10/100 Base -TX, 5xRJ45, neupravljivi za montažu na DIN šinu Napajanje: 12/24VDC, max 2,2W. (ŠxVxD) - 25mm x 114mm x 79mm Tip: SPIDER-SL-20-5T1999999SZ9HHHH proizvođač: Hirschmann ili slično | Ethernet switch 5x10/100 Base-TX, 5xRJ45, unmanageable for mounting on a DIN rail Power supply: 12/24VDC, max 2.2W. (WxHxD) - 25mm x 114mm x 79mm Type: SPIDER-SL-20-5T1999999SZ9HHHH Manufacturer: Hirschmann or similar | kom/ pcs |  | 2 | 0
121. |  | Ethernet utičnica za montažu na din šinu Tip: proizvođač: Schrack Technik ili slično | Ethernet socket for mounting on a din rail Type: Manufacturer: Schrack Technik or similar | kom/ pcs |  | 4 | 0
122. |  | Nabavka, isporuka i montaža Metasys® Network Control Engine (NCE) 10 univerzalnih ulaza, 8 binarna ulaza, 4 analogna izlaza, 7 binarna izlaza, 4 konfigurabilna izlaza, 32-bitni mikroprocesor, Samoadaptivni PID. Sa FC Bus trunkom za integraciju BACnet MS/TP protokola. Sa BACnet IP komunikacijom za BMS. Sa integrisanim Web serverom. Sa opcijama za zadavanje vremenskih rasporeda, slanjem e-mail-a. Sa mogućnošću 3rd party integracije. BTL sertifikovan uređaj. Tip: MS-NCE2560-0 Proizvođač: Johnson Control ili slično. | Supply, delivery and installation of Metasys® Network Control Engine (NCE) 10 universal inputs, 8 binary inputs, 4 analogue outputs, 7 binary outputs, 4 configurable outputs, 32-bit microprocessor, Self-adaptive PID. With FC Bus trunk for BACnet MS/TP protocol integration. With BACnet IP communication for BMS. With an integrated Web server. With options for setting time schedules by sending an e-mail. With the possibility of 3rd party integration. BTL-certified device. Type: MS-NCE2560-0 Manufacturer: Johnson Controls or similar. | kom/ pcs |  | 1 | 0
123. |  | Metasys® Input/Output ekspanzionog modula sa 8 digatalnih ulaza i 8 digitalnih izlaza. Sa BACnet MS/TP karticom. Napajanje: 24 VAC. BTL sertifikovan uređaj. Tip: MS-IOM3731-0 Proizvođač: Johnson Control ili slično. | Metasys® Input/Output expansion module with 8 digital inputs and 8 digital outputs. With BACnet MS/TP card. Power supply: 24 VAC. BTL-certified device. Type: MS-IOM3731-0 Manufacturer: Johnson Controls or similar. | kom/ pcs |  | 1 | 0
124. |  | Metasys® Input/Output ekspanzionog modula sa 16 binarnih ulaza. Sa BACnet MS/TP karticom. Napajanje: 24 VAC. BTL sertifikovan uređaj. Tip: MS-IOM3721-0 Proizvođač: Johnson Control ili slično. | Metasys® Input/Output expansion module with 16 binary inputs. With BACnet MS/TP card. Power supply: 24 VAC. BTL-certified device. Type: MS-IOM3721-0 Manufacturer: Johnson Controls or similar. | kom/ pcs |  | 1 | 0
125. |  | Sitan montažni materijal | Necessary assembly material | pauš/LS |  | 1 | 0
126. |  | Šemiranje ormara | Planning of the cabinet according to installation schemes | pauš/LS |  | 1 | 0
127. |  | Programiranje kontrolera | Controller programming. | pauš/LS |  | 1 | 0
128. |  | Povezivanje ormara, podešavanje parametara automatike, funkcionalno ispitivanje i puštanje u rad. | Connecting cabinets, setting automation parameters, functional testing and commissioning. | pauš/LS |  | 1 | 0
I c |  | RAZVODNI ORMAR ROA - VOD | DISTRIBUTION CABINET ROA-VOD |  |  | Ukupno | 0
I. |  | RAZVODNI ORMARI AUTOMATIKE | DISTRIBUTION CABINETS OF AUTOMATION |  |  | Ukupno | 0
II. |  | OSTALA OPREMA I RADOVI ZA CSNU | OTHER EQUIPMENT AND WORKS FOR CSNU
129. |  | PC računar, sledećih karakteristika, ili slično: 2.4 GHz Pentium® i5 processor with 500 GB hard disk, DVD drive, Мemorija 4 GB RAM Operativni sistem Microsoft® Windows® 7 OS Professional, Enterprise, and Ultimate Editions (32-bit) with SP1 (Includes Microsoft IIS Version 7.5) Microsoft Internet Explorer® Version 6.x, 7.0, or 8.0 Java® Runtime Environment (JRE) 1.6.0_23 Monitor 27"+, 1 optički miš 1 tastatura sa 102 tastera 1 mrežna kartica 100/10 Mbps Licencirani MS WINDOWS 7 komplet svih potrebnih kablova za vezu Napajanje: 220V, 50 Hz. Tip: Optiplex Proizvođač: Dell ili sl. | PC computer, with the following characteristics or similar: 2.4 GHz Pentium® i5 processor with 500 GB hard disk, DVD drive, Memory 4 GB RAM Operating system Microsoft® Windows® 7 OS Professional, Enterprise, and Ultimate Editions (32-bit) with SP1 (Includes Microsoft IIS Version 7.5) Microsoft Internet Explorer® Version 6.x, 7.0, or 8.0 Java® Runtime Environment (JRE) 1.6.0_23 Monitor 27""+, 1 optical mouse 1 keyboard with 102 keys 1 network card 100/10 Mbps Licensed MS WINDOWS 7 a set of all the necessary connection cables Power supply: 220V, 50 Hz. Type: Optiplex Manufacturer: Dell or similar. | kom/ pcs |  | 1 | 0
130. |  | Laserski štampač HP P1102, ili sličan | Laser printer HP P1102 or similar | kom/ pcs |  | 1 | 0
131. |  | Modbus upravljački drajveri za integraciju uređaja na BMS sistem | Modbus control drivers for device integration to the BMS system | pauš/LS |  | 1 | 0
132. |  | CSNU softver za centralizovani rad i nadzor nad tehničkim postrojenjima, vizuelizaciju procesa, izdavanje alarma i procesiranje odgovora, protokolisanje i evaluaciju podataka i optimizaciju procesa. Ethernet mrežni program u Microsoft Windows okruženju je modularne strukture i omogućava da se celokupan sistem može individualno konfigurisati u skladu sa zahtevima korisnika. * Standardni korisnički interface kroz Windows i 2000/NT/XP/Vista/7. * Mrežna komunikacija bazirana na TCP/IP tehnologiji * Dinamičke slike postrojenja * Tekstualni prozori, liste i osnovni protokoli * Password zaštita * Štampanje u standardnom formatu * Štampanje alarma i događaja * Liste alarma i indikacija alarma na ekranu *Monitoring graničnih vrednosti analognih vel. * Izdavanje digitalnih i analognih komandi sa slike postrojenja * Podešavanje set-point vrednosti * Vremenske funkcije/godišnji kalendar * Vizuelizacija podataka iz istorijske banke podataka(HDB)(tabelarno, grafički -trend kr.) Tip: MS-ADSLE5U-0 proizvođač: Johnson Control ili sl. | CSNU software for centralized operation and supervision of technical facilities, process visualization, alarm issuance and response processing, data logging and evaluation, and process optimization. The Ethernet network program in the Microsoft Windows environment has a modular structure and allows the entire system to be individually configured according to the user's requirements. * Standard user interface through Windows and 2000/NT/XP/Vista/7. * Network communication based on TCP/IP technology * Dynamic plant images * Text windows, lists and basic protocols * Password protection * Printing in the standard format * Printing of alarms and events * Alarm lists and alarm indications on the screen *Monitoring of limit values of analogue data. * Issuing digital and analogue commands from the plant image * Setting the set-point value * Time functions/annual calendar * Visualization of data from the historical data bank (HDB) (tabular, graphic - trend kr.) Type: MS-ADSLE5U-0 manufacturer: Johnson Control or similar. | pauš/LS |  | 1 | 0
133. |  | Provera ožičenja i komunikacije. Usklađivanje svih parametara komunikacije. Kalibracija opreme u polju, adresiranje kontrolera | Checking wiring and communication. Coordination of all communication parameters. Field equipment calibration, controller addressing | pauš/LS |  | 1 | 0
134. |  | Izrada aplikativnog softvera i odgovarajućih grafičkih ekrana. | Development of application software and corresponding graphic screens. | pauš/LS |  | 1 | 0
135. |  | Integracija na BMS opreme koja komunicira preko ModBUS protokola | Integration on BMS equipment that communicates via the ModBUS protocol | kom/ pcs |  | 1 | 0
136. |  | Socomec UPS NeTYS PE 850VA/480W, 230V, 50/60Hz, AVR, RJ45, USB, Line interactive, Step wave | Socomec UPS NeTYS PE 850VA/480W, 230V, 50/60Hz, AVR, RJ45, USB, Line interactive, Step wave | kom/ pcs |  | 1 | 0
137. |  | Puštanje sistema u rad, test softvera, test hardvera, podešavanja | System commissioning, software test, hardware test, settings | pauš/LS |  | 1 | 0
138. |  | Obuka tehničkog osoblja krajnjeg korisnika | Training of user technical staff | pauš/LS |  | 1 | 0
139. |  | Ostali sitni i nespicificirani poslovi i oprema | Necessary assembly material and unspecified jobs and equipment | pauš/LS |  | 1 | 0
140. |  | Izrada projekta odrzavanja CSNU i EMP | Preparation of a maintenance design for CSNU and EMP | pauš/LS |  | 1 | 0
II. |  | OSTALA OPREMA I RADOVI ZA CSNU | OTHER EQUIPMENT AND WORKS FOR CSNU |  |  | Ukupno | 0
III. |  | OPREMA U POLJU | EQUIPMENT IN THE FIELD
|  | Toplotna podstanica | Heat substation
141. |  | Štapni senzor temperature sa mesinganom čaurom za montažu u toplotnoj podstanici Dužina: 192mm Merni opseg: -40...120 °C Izlazni signal: Pt1000 Tip: TS-6360D-B10 + TS-6300W-F400 proizvođač: Johnson Controls ili slično | Rod temperature sensor with brass sleeve for mounting in the heat substation Length: 192mm Measuring range: -40-120 °C Output signal: Pt1000 Type: TS-6360D-B10 + TS-6300W-F400 Manufacturer: Johnson Controls or similar | kom/ pcs |  | 11 | 0
142. |  | Štapni senzor temperature sa mesinganom čaurom za montažu na bojlere i akumulatore toplote u toplotnoj podstanici Dužina: 290mm Merni opseg: -40...120 °C Izlazni signal: Pt1000 Tip: TS-6360D-C10 + TS-6300W-I400 proizvođač: Johnson Controls ili slično | Rod temperature sensor with brass sleeve for mounting on boilers and heat accumulators in the heat substation Length: 290mm Measuring range: -40...120 °C Output signal: Pt1000 Type: TS-6360D-C10 + TS-6300W-I400 Manufacturer: Johnson Controls or similar | kom/ pcs |  | 2 | 0
143. |  | Senzor pritiska za montažu u toplotnoj podstanici Merni opseg: -100 to 800 kPa (-1 to 8 bar) Izlazni signal: 0-10V Napajanje: 12V-30V Tip: P499-VBS-401C proizvođač: Johnson Controls ili slično | Pressure sensor for mounting in the heat substation Measuring range: -100 to 800 kPa (-1 to 8 bar) Output signal: 0-10V Power supply: 12V-30V Type: P499-VBS-401C Manufacturer: Johnson Controls or similar | kom/ pcs |  | 2 | 0
144. |  | Granični termostat za bojler sa čaurom Opseg: 40..120°C tip: A19ABC-9011 proizvođač: Johnson Controls ili slično | Limit thermostat for boiler with sleeve Range: 40 - 120°C type: A19ABC-9011 Manufacturer: Johnson Controls or similar | kom/ pcs |  | 2 | 0
145. |  | Spoljnji senzor temperature Opseg: -40 ... 50°C Izlazni signal: Pt1000 Tip: TS-6360E-000 proizvođač: Johnson Controls ili slično | External temperature sensor Range: -40 - 50°C Output signal: Pt1000 Type: TS-6360E-000 Manufacturer: Johnson Controls or similar | kom/ pcs |  | 1 | 0
146. |  | Monofazna OG priključnica sa zaštitnim kontaktom 230V, 16A, za montažu na zid Schrack Technik ili slično. | Monophase OG socket with protective contact 230V, 16A, for mounting on the wall Schrack Technik or similar. | kom/ pcs |  | 1 | 0
147. |  | Gateway Resol Datalogger DL3 za povezivanje solarne stanice na BMS Napajanje:100 – 240 V~, 1A/12 V⎓, 1 A (Level 6) Montaža ; na zidu Data interface: 6 x VBus® (slave), 1 x SD memory card slot, 1 x LAN (10 / 100), 1 x USB master Protokol: Bacnet IP tip: Datalogger DL2Plus | Gateway Resol Datalogger DL3 for connecting the solar station to the BMS Power supply: 100 – 240 V~, 1A/12 V⎓, 1 A (Level 6) Assembly; on the wall Data interface: 6 x VBus® (slave), 1 x SD memory card slot, 1 x LAN (10 / 100), 1 x USB master Protocol: Bacnet IP type: Datalogger DL2Plus | kom/ pcs |  | 1 | 0
|  | Klima komora | Air chamber
148. |  | El. motorni pogon žaluzine sa povratnom oprugom. Upravljački signal: Proporcionalni 0-10V Obrtni moment: 16 Nm Napajanje: 24 VAC. Tip: SMQ24A-MF Proizvođač: Belimo ili slično | Electrical window-blind motor drive with return spring. Control signal: Proportional 0-10V Torque: 16 Nm Power supply: 24 VAC. Type: SMQ24A-MF Manufacturer: Belimo or similar | kom/ pcs |  | 3 | 0
149. |  | El. motorni pogon žaluzine sa povratnom oprugom. Upravljački signal: Proporcionalni 0-10V Obrtni moment: 4 Nm Napajanje: 24 VAC. Tip: LF24-SR Proizvođač: Belimo ili slično | Electrical window- blind motor drive with return spring. Control signal: Proportional 0-10V Torque: 4 Nm Power supply: 24 VAC. Type: LF24-SR Manufacturer: Belimo or similar | kom/ pcs |  | 1 | 0
150. |  | CO2 transmiter za mjerenje CO2 nivo i temperature u HVAC sistemima. Montira se na kanalu klima komore tip: CD-P1000-00-00 proizvođač: Johnson Controls ili slično | CO2 transmitter for measuring CO2 level and temperature in HVAC systems. It is mounted on the channel of the air conditioning chamber type: CD-P1000-00-00 Manufacturer: Johnson Controls or similar | kom/ pcs |  | 1 | 0
151. |  | Senzor temperature za montažu na kanalu klima komore tip: TS-6360D-C10 + TS-6300D-000 proizvođač: Johnson Controls ili slično | Temperature sensor for installation on the pipeline of the air conditioning chamber type: TS-6360D-C10 + TS-6300D-000 Manufacturer: Johnson Controls or similar | kom/ pcs |  | 2 | 0
152. |  | Mraz termostat Opseg: -5..12°C Tip: 270XT-95008 proizvođač: Johnson Controls ili slično | Frost thermostat Range: -5..12°C Type: 270XT-95008 Manufacturer: Johnson Controls or similar | kom/ pcs |  | 1 | 0
153. |  | Spoljnji senzor temperature Opseg: -40 ... 50°C Izlazni signal: Pt1000 Tip: TS-6360E-000 + + TS-6300W-F400 proizvođač: Johnson Controls ili slično | External temperature sensor Range: -40 ... 50°C Output signal: Pt1000 Type: TS-6360E-000 + + TS-6300W-F400 Manufacturer: Johnson Controls or similar | kom/ pcs |  | 1 | 0
154. |  | Kanalni termostat-regulacioni Tip: KTR-1 Proizvođač: Feniks bb ili slično | Channel thermostat-regulator Type: KTR-1 Manufacturer: Feniks bb or similar | kom/ pcs |  | 2 | 0
155. |  | Diferencijalni presostat Opseg: 50...400 Pa Tip: P233A-4-PKC Proizvođač: Johnson Controls ili slično | Differential pressure switch Range: 50...400 Pa Type: P233A-4-PKC Manufacturer: Johnson Controls or similar | kom/ pcs |  | 3 | 0
|  | Ostalo | Other
156. |  | Kanalni termostat Tip:KTR-1 Proizvođač: Feniks bb ili slično | Channel thermostat Type: KTR-1 Manufacturer: Feniks bb or similar | kom/ pcs |  | 1 | 0
157. |  | Senzor temperature za montažu na zidu. Izlazni signal: 0-10V proporcionalno mjerenoj temperaturi Napajanje: 15VDC tip:RS-1140-0000 proizvođač: Johnson Controls ili slično | Temperature sensor for wall mounting. Output signal: 0-10V proportional to the measured temperature Power supply: 15VDC type: RS-1140-0000 Manufacturer: Johnson Controls or similar | kom/ pcs |  | 50 | 0
158. |  | Touchscreen Advanced Display -za zbornicu Slobodno programabilan interfejs TFT 64K boja, LED pozadinsko osvetljenje Komunikacija: BACnet MS/TP, BACnet IP Veličina: 4.7" , Napajanje: 24 VAC/DC, 300 mA Stepen zaštite: IP66 (IP20 nazad) Montaža na zidu CE znak u skladu sa EMC i RoHS direktivama Tip: TAD4701-0 + Proizvođač: Johnson Controls ili slično | Touchscreen Advanced Display - for the conference room Freely programmable interface TFT 64K colour, LED backlight Communication: BACnet MS/TP, BACnet IP Size: 4.7" , Power supply: 24 VAC/DC, 300 mA Degree of protection: IP66 (IP20 back) Wall mounting CE mark in accordance with EMC and RoHS directives; Type: TAD4701-0 + Manufacturer: Johnson Controls or similar | kom/ pcs |  | 1 | 0
159. |  | Touchscreen Advanced Display-za upravljanje radom klima komore Slobodno programabilan interfejs TFT 64K boja, LED pozadinsko osvetljenje Komunikacija: BACnet MS/TP, BACnet IP Veličina: 7" , 480×272 px, 16:9 Napajanje: 24 VAC/DC, 300 mA Stepen zaštite: IP66 (IP20 nazad) Montaža na zidu kabineta profesora fizickog vaspitanja. Masa : 0.6kg CE znak u skladu sa EMC i RoHS direktivama Tip: TAD0701-0 SA OKVIROM ZA MONTAŽU NA ZIDU Proizvođač: Johnson Controls ili slično | Touchscreen Advanced Display-for controlling the operation of the air conditioning chamber Freely programmable interface TFT 64K colour, LED backlight Communication: BACnet MS/TP, BACnet IP Size: 7", 480×272 px, 16:9 Power supply: 24 VAC/DC, 300 mA Degree of protection: IP66 (IP20 back) Mounting on the wall of the physical education professor's office. Weight: 0.6 kg CE mark in accordance with EMC and RoHS directives Type: TAD0701-0 WITH FRAME FOR WALL MOUNTING Manufacturer: Johnson Controls or similar | kom/ pcs |  | 1 | 0
160. |  | Programiranje HMI kontrolera | HMI controller programming | kom/ pcs |  | 2 | 0
161. |  | Montaža i povezivanje opreme u polju (povezivanje ventilatora, motora za prozore, komunikacije fan coila, rekuperatora, agregata i toplotnih, montaža i povezivanje opreme automatike u toplotnoj podstanici i klima komori, montaža i povezivanje senzora temperature i zidnih panela. | Installation and connection of equipment in the field (connection of fans, window motors, communication of fan coils, recuperators, aggregates and heat, installation and connection of automation equipment in the heating substation and air conditioning chamber, installation and connection of temperature sensors and wall panels. | pauš/LS |  | 1 | 0
III. |  | OPREMA U POLJU | EQUIPMENT IN THE FIELD |  |  | Ukupno | 0
IV. |  | KABLOVI, KABLOVSKI REGALI I CIJEVI | CABLES, CABLE RAILS AND PIPES
162. |  | NHXHX-J FE180/E90 4x2.5mm2 | NHXHX-J FE180/E90 4x2.5mm2 | m1 |  | 110 | 0
163. |  | N2XH-J 2x1.5 mm2 | N2XH-J 2x1.5 mm2 | m1 |  | 70 | 0
164. |  | N2XH-J 3x1.5 mm2 | N2XH-J 3x1.5 mm2 | m1 |  | 570 | 0
165. |  | N2XH-J 4x1.5 mm2 | N2XH-J 4x1.5 mm2 | m1 |  | 760 | 0
166. |  | N2XH-J 3x2.5 mm2 | N2XH-J 3x2.5 mm2 | m1 |  | 150 | 0
167. |  | N2XH-J 4x2.5 mm2 | N2XH-J 4x2.5 mm2 | m1 |  | 120 | 0
168. |  | N2XH-J 4x4 mm2 | N2XH-J 4x4 mm2 | m1 |  | 20 | 0
169. |  | N2XH-J 5x6 mm2 | N2XH-J 5x6 mm2 | m1 |  | 40 | 0
170. |  | J-H(ST)H 1x2x0.8 mm2 | J-H(ST)H 1x2x0.8 mm2 | m1 |  | 350 | 0
171. |  | J-H(ST)H 2x2x0.8 mm2 | J-H(ST)H 2x2x0.8 mm2 | m1 |  | 1100 | 0
172. |  | J-H(ST)H 3x2x0.8 mm2 | J-H(ST)H 3x2x0.8 mm2 | m1 |  | 15 | 0
173. |  | J-H(ST)H 4x2x0.8 mm2 | J-H(ST)H 4x2x0.8 mm2 | m1 |  | 60 | 0
174. |  | J-H(ST)H 5x2x0.8 mm2 | J-H(ST)H 5x2x0.8 mm2 | m1 |  | 150 | 0
175. |  | J-H(ST)H 7x2x0.8 mm2 | J-H(ST)H 7x2x0.8 mm2 | m1 |  | 10 | 0
176. |  | LiYCY 2x1mm2 | LiYCY 2x1mm2 | m1 |  | 110 | 0
177. |  | LiYCY 4x1mm2 | LiYCY 4x1mm2 | m1 |  | 5600 | 0
178. |  | LiYCY 4x1.5mm2 | LiYCY 4x1.5mm2 | m1 |  | 40 | 0
179. |  | LiHCH FE180/PH90 4x1.5mm2 | LiHCH FE180/PH90 4x1.5mm2 | m1 |  | 80 | 0
180. |  | Ethernet kabal FTP CAT 6 | Ethernet cablel FTP CAT 6 | m1 |  | 500 | 0
181. |  | Traka FeZn 25x4 mm | Strip FeZn 25x4 mm | m1 |  | 70 | 0
182. |  | Nosač FeZn trake | Holder of FeZnstrip | kom/ pcs |  | 15 | 0
183. |  | Ukrsni komadi za FeZn traku | Cross pieces for FeZn strip | kom/ pcs |  | 20 | 0
184. |  | Bakarna pletenica za izjednačacanje potencijala 10mm2 sa odgovarajućim završecima, prosječne dužine 0,6 | Copper braid for potential equalization 10mm2 with matching terminations, average length 0.6 | kom/ pcs |  | 50 | 0
185. |  | P/F izolovani provodnik za povezivanje ormara i metalnih djelova sa potrebnim materijalom za povezivanje | P/F insulated conductor for connecting cabinets and metal parts with the necessary connecting material | m1 |  | 150 | 0
186. |  | Perforirani kablovski regal RKSM 300x60 mm sa nosačima RKSM OBO ili sličan | Perforated cable rail RKSM 300x60 mm with brackets RKSM OBO or similar | m1 |  | 10 | 0
187. |  | Perforirani kablovski regal RKSM 100x60 mm sa nosačima RKSM OBO ili sličan | Perforated cable rail RKSM 100x60 mm with brackets RKSM OBO or similar | m1 |  | 290 | 0
188. |  | Perforirani kablovski regal RKSM 50x60 mm sa nosačima RKSM OBO ili sličan | Perforated cable rail RKSM 50x60 mm with supports RKSM OBO or similar | m1 |  | 60 | 0
189. |  | Rebrasto halogenfree crijevo HFX 20/14,1 sa gumom | Ribbed halogen-free hose HFX 20/14,1 with rubber | m1 |  | 1400 | 0
190. |  | Rebrasto halogenfree HFX 25/19 sa gumom | Ribbed halogen-free HFX 25/19 with rubber | m1 |  | 250 | 0
191. |  | Metalno plastificirano gibljivo crijevo (SAPA) fi21 za razvod negorivih kablova | Metal plasticized flexible hose (SAPA) fi21 for distribution of non-combustible cables. | m1 |  | 1000 | 0
192. |  | Metalno plastificirano gibljivo crijevo (SAPA) fi26 za razvod negorivih kablova | Metal plasticized flexible hose (SAPA) fi26 for distribution of non-combustible cables. | m1 |  | 430 | 0
193. |  | Zaštitna plastična ravna samogasiva cijev VRM 20/17,4 sa obujmicom za razvod kablova unutar klima komora | Protective plastic flat self-extinguishing pipe VRM 20/17.4 with clamp for cable distribution inside air conditioning chambers | m1 |  | 100 | 0
194. |  | Nespeficirani montažni materijal | Unspecified assembly material | pauš/LS |  | 1 | 0
IV. |  | KABLOVI, KABLOVSKI REGALI I CIJEVI | CABLES, CABLE RAILS AND PIPES |  |  | Ukupno / Total | 0
I. |  | RAZVODNI ORMARI AUTOMATIKE | DISTRIBUTION CABINETS OF AUTOMATION |  |  | Ukupno / Total | 0
II. |  | OSTALA OPREMA I RADOVI ZA CSNU | OTHER EQUIPMENT AND WORKS FOR CSNU |  |  | Ukupno / Total | 0
III. |  | OPREMA U POLJU | EQUIPMENT IN THE FIELD |  |  | Ukupno / Total | 0
IV. |  | KABLOVI, KABLOVSKI REGALI I CIJEVI | CABLES, CABLE RAILS AND PIPES |  |  | Ukupno / Total | 0
3.3. |  | UKUPNO BMS i EMP | TOTAL BMS AND EMP |  |  |  | 0

## 4.1. termot.inst-HVAC
Program obrazovanja Crne Gore / The education program of Montenegro
Predmjer - Izgradnja nove OŠ "Vladimir Nazor"/ Bill of Quantity - Construction of new Elementary School "Vladimir Nazor" TERMOTEHNIČKE INSTALACIJE / THERMOTECHNICAL INSTALLATION (HVAC)
br/No | predmet/ subject | NASLOV | NAME | mjerna jedinica/ UNIT | pred.cijena/ unit price in € | Količina/ Quantity | Cijena u eurima (bez PDV-a)/ Amount in € (without VAT)
(a) | (b) | (c) |  | ( d ) | (e) | (f) | (g=e*f)
4.1. |  | TERMOTEHNIČKE INSTALACIJE
PREDMJER I PREDRAČUN TERMOTEHNIČKIH INSTALACIJA / BILL OF QUANTITY OF THERMOTECHNICAL INSTALLATION
I. |  | TOPLOTNA PUMPA I PODSTANICA ZA GRIJANJE I HLAĐENJE ŠKOLE | HEAT PUMP AND SUBSTATION FOR HEATING AND COOLING OF THE SCHOOL
1. |  | Isporuka i montaža vazduhom hlađenje toplotne pumpe za spoljašnju ugradnju, reverzibilne na freonskoj strani, sa parcijalnom rekuperacijom toplote - desuperhiterom (agregat ima 4 cijevi: par cijevi za hladnu/toplu vodu u zavisnosti od zadatog moda – hlađenje ili grijanje, par cijevi za toplu vodu od rekuperacije). Agregat se isporučuje sa daljinskim kontrolerom RCMRX, komunikacijskom karticom CMSC9 (Modbus), antivibracionim osloncima AMMX, kompletom od dvije inverterske pumpe (radne i rezervne) na strani potrošnje 2PMV i svim neophodnim elementima automatike. Agregat je proizvod firme "CLIVET" S.p.A. Italija ili sl, sledećih karakteristika: tip: WSAN-YSC4 120.4 rashladni fluid: R32 temperatura vode u režimu hlađenja: 12/7°C temperatura vode u režimu grijanja: 40/45°C rashladni kapacitet na +37°C: 313 kW potrošnja struje na hlađenju: 109 kW EER=2,87; grejni kapacitet -6°C: 242 kW; potrošnja struje na grijanju: 97.8 kW; COP=2,48; napajanje: 400-3Ph-50Hz; broj i tip kompresora: 4, Scroll; broj rashladnih krugova: 2; dimenzije: 4114x2250x2520 mm (WxDxH); masa: 2890 kg | Delivery and installation of air-cooled heat pump for external installation, reversible on the freon side, with partial heat recovery - desuperheater (the unit has four pipes: the pair of pipes for cold/hot water depending on the set mode - cooling or heating, the pair of pipes for hot water from recovery). The unit is delivered with a remote controller RCMRX, the communication card CMSC9 (Modbus), anti-vibration supports AMMX, the set of two inverter pumps (working and reserve) on the consumption side 2PMV and all necessary automatic elements. The unit is a product of the company "CLIVET" S.p.A. Italy or similar, with the following characteristics: type: WSAN-YSC4 120.4; coolant: R32, water temperature in cooling mode: 12/7°C; water temperature in heating mode: 40/45°C; cooling capacity at +37°C: 313 kW; power consumption for cooling: 109 kW; EER=2,87; heating capacityt -6°C: 242 kW; electricity consumption for heating: 97.8 kW; COP=2,48; power supply: 400-3Ph-50Hz; number and type of compressors: 4, Scroll; number of cooling circuits: 2; dimensions: 4114x2250x2520 mm (WxDxH); mass: 2890 kg | komplet/ set |  | 2 | 0
2. |  | Isporuka i montaža predizolovanih cijevi i fitinga sledećih dimenzija i količina: Predizolovane čelične šavne cijevi, spiralno zavarene (zavar V=1, ispitana na 40 bar-a trajno sa pikovima na 80 bar-a 10 sek), materijal St 37.0 odnosno Č0361 po DIN 1626, dimenzije i mase prema DIN-u 2458, cijevni završeci pripremljeni za zavarivanje po DIN-u 2559. Termička izolacija od PUR pene, prosječne gustine 80 kg/m3. Hidro izolacija od PEHD omotača obrađenog korona efektom. Duž cijevi su postavljene žice za detekciju vlage u izolaciji. Sve po standardu EN 253 za predizolovane cijevi: | Delivery and installation of pre-insulated pipes and fittings of the following dimensions and quantities: Pre-insulated steel seam pipes, spirally welded (weld V=1, tested at 40 bar permanently with peaks at 80 bar for 10 seconds), material St 37.0 or Č0361 according to DIN 1626, dimensions and weights according to DIN 2458, pipe ends prepared for welding according to DIN 2559. Thermal insulation from PUR foam, average density 80 kg/m3. Hydro insulation from PEHD sheath treated with corona effect. Wires for detecting moisture in the insulation are placed along the pipe. All according to the EN 253 standard for pre-insulated pipes:
|  | NO80 (Ø88,9x3,2 mm) | NO80 (Ø88,9x3,2 mm) | m1 |  | 120 | 0
|  | NO150 (Ø168,3x4,5 mm) | NO150 (Ø168,3x4,5 mm) | m1 |  | 110 | 0
3. |  | Predizolovane čvrste tačke od čeličnih bešavnih cijevi materijala St 35.8, odnosno Č1212, izolovane PUR pjenom na bazi ciklopentana i PEHD omotačem obrađenoh korona efektom, po standardu EN 448: | Pre-insulated solid points made of steel seamless pipes of material St 35.8, i.e. Č1212, insulated with cyclopentane-based PUR foam and PEHD sheath treated with corona effect, according to EN 448 standard:
|  | DN80 | DN80 | kom/pcs |  | 2 | 0
|  | DN150 | DN150 | kom/pcs |  | 2 | 0
4. |  | Čelični predizolovani glatki lukovi (ne segmentnih) od bešavnih cijevi materijala St 35.8, odnosno Č1212 po važećoj evropskoj normi EN 448, izolovanih PUR pjenom u PEHD omotaču: | Steel pre-insulated smooth arches (not segmented) made of seamless pipes of material St 35.8, i.e. Č1212 in accordance with the current European standard EN 448, insulated with PUR foam in PEHD sheats:
|  | DN80 | DN80 | kom/pcs |  | 8 | 0
|  | DN150 | DN150 | kom/pcs |  | 8 | 0
5. |  | Termoskupljajuće PEHD spojnica za predizolovane cijevi od umreženog polietilena minimalne dužine 700mm sa pratećom opremom (trake, buksne, odstojnici i čepovi), izrađenih po standardu EN489: | Heat-shrinkable PEHD connectors for pre-insulated pipes, made from cross-linked polyethylene with a minimum length of 700mm with accessories equipment (strips, bushings, spacers and plugs), made according to the EN489 standard:
|  | DN80 | DN80 | kom/pcs |  | 36 | 0
|  | DN150 | DN150 | kom/pcs |  | 36 | 0
6. |  | Zaptivača za montažu pri prolasku kroz zid za sprečavanje izlivanja vode prilikom prolaza kroz zid. Sastoji se od specijalnog profilisanog neoprenskog prstena prema DIN 18337: | Sealant for installation for passing through the wall to prevent water spillage when passing through the wall. It consists of the unique profiled neoprene ring according to DIN 18337:
|  | DN80 | DN80 | kom/pcs |  | 2 | 0
|  | DN150 | DN150 | kom/pcs |  | 2 | 0
7. |  | Kompenzacioni jastuk za prihvatanje dilatacija predizolovanih cijevi standardne debljine 40 mm i dužine 1000 mm. | Compensation cushion for accepting expansions of pre-insulated pipes with a standard thickness of 40 mm and a length of 1000 mm. | kom/pcs |  | 48 | 0
8. |  | Traka upozorenja (isporučuju se u rolni dužine 250 m): | Warning tape (supplied in a 250 m long roll): | komplet/set |  | 1 | 0
9. |  | Izrada, isporuka i montaža hidrauličke skretnice (koja ujedno služi i kao akumulacija hladne/tople vode za hlađenje/grijanje škole) sledećih karakteristika: * dimenzije posude: ∅1200x2000 mm * zapremina vode: cca 2000 l * sa dvije unutrašnje horizontalne pregrade od perforiranog lima debljine 3 mm, sa otvorima Ø5 mm, svijetla površina min. 50% * priključci na primaru: 2xDN200 (dovod u gornjoj zoni iznad gornje perforirane ploče, odvod u donjoj zoni ispod donje perforirane ploče) * priključci na sekundaru: 2xDN200 (polaz u gornjoj zoni iznad gornje perforirane ploče, povrat u donjoj zoni ispod donje perforirane ploče) * priključak R3/4" sa slavinom za ozračivanje na vrhu posude * priključak R1" za pražnjenje na dnu posude * Izolacija obračunata posebno | Producing, delivering and installation of the hydraulic switch (which also serves as an accumulation of cold/hot water for cooling/heating the school) with the following characteristics: * container dimensions: ∅1200x2000 mm; * water volume: cca 2000 l; * with two internal horizontal partitions made of perforated sheet metal 3 mm thick, with openings Ø5 mm, bright surface min. 50% * connections on the primary: 2xDN200 (supply in the upper zone above the upper, perforated plate, drain in the lower zone below the lower perforated plate); * connections to the secondary: 2xDN200 (outlet in the upper zone above the upper, perforated plate, return in the lower zone below the lower perforated plate); * connection R3/4" with tap for air-release on the top of the bowl; * connection R1" for emptying at the bottom of the container; * Insulation calculated separately | komplet/set |  | 1 | 0
10. |  | Izrada, isporuka i montaža hidrauličke skretnice (koja ujedno služi i kao akumulacija tople vode za grijanje sanitarne tople vode) sledećih karakteristika: * dimenzije posude: ∅1200x1000 mm * zapremina vode: cca 1000 l * sa dvije unutrašnje horizontalne pregrade od perforiranog lima debljine 3 mm, sa otvorima Ø5 mm, svijetla površina min. 50% * priključci na primaru: 2xDN100 (dovod u gornjoj zoni iznad gornje perforirane ploče, odvod u donjoj zoni ispod donje perforirane ploče) * priključci na sekundaru: 2xDN100 (polaz u gornjoj zoni iznad gornje perforirane ploče, povrat u donjoj zoni ispod donje perforirane ploče) * priključak R3/4" sa slavinom za ozračivanje na vrhu posude * priključak R1" za pražnjenje na dnu posude * Izolacija obračunata posebno | Producing, delivery and installation of the hydraulic switch (which also serves as hot water storage for heating sanitary hot water) with the following characteristics: * container dimensions: ∅1200x1000 mm; * volume of water: approx. 1000 l; * with two internal horizontal partitions made of perforated sheet metal 3 mm thick, with openings Ø5 mm, bright surface min. 50%; * connections on the primary: 2xDN100 (supply in the upper zone above the upper, perforated plate, drain in the lower zone below the lower perforated plate); * connections to the secondary: 2xDN100 (outlet in the upper zone above the upper, perforated plate, return in the lower zone below the lower perforated plate); * connection R3/4" with tap for air-release on the top of the bowl; * connection R1" for emptying at the bottom of the container; * Insulation calculated separately | komplet/ set |  | 1 | 0
11. |  | Isporuka i mornaža bojlera sanitarne tople vode sa dva izmjenjivača, zapremine 2000 l, termoizolovan; površine grejnih spirala: donje 4,5 m2, gornja 3 m2; dodatni elektro grijač 12 kW, tip Solarcell BIV R2BC, proizvođača "Viessmann" ili sl. | Delivery and installation of the hot water boiler with two exchangers, volume 2000 l, thermally insulated; heating coil surfaces: lower 4.5 m2, upper 3 m2; additional electric heater 12 kW, type Solarcell BIV R2BC, manufactured by "Viessmann" or similar. | komplet/ set |  | 2 | 0
|  | Isporuka i montaža cirkulacionih pumpi proizvođača "Grundfos" - Danska ili sl; sledećih tipova, karakteristika i količina: | Delivery and installation of circulation pumps manufactured by "Grundfos" - Denmark or similar; of the following types, characteristics and quantities:
12. |  | Tip: TPE 100-200/4 A-F-A-BAQE-MWA (za cirkulaciju hladne / tople vode u krugu: hidraulična skretnica za školu - fan coil aparati) * protok vode: 121430 l/h * napor: 1155 kPa * medij: tehnička voda, ljeti 7/12°C, zimi 45/40°C * napajanje: 380V-3ph-50Hz * snaga: 7,5 kW * elektronska kontrola | Type: TPE 100-200/4 A-F-A-BAQE-MWA(for cold/hot water circulation in the circuit: hydraulic switch for school - fan coil devices); * water flow: 121430 l/h; * effort: 1155 kPa; * medium: technical water,in summer 7/12°C, in winter 45/40°C; * Power supply: 380V-3ph-50Hz; * Power: 7,5 kW; * Electronic control | kom/ pcs |  | 2 | 0
13. |  | Tip: MAGNA3 65-150 F (za cirkulaciju tople vode u krugu: desuperhiter - hidraulična skretnica za STV) * protok vode: 22100 l/h * napor: 100 kPa * medij: tehnička voda, 45/40°C * napajanje: 220V-1ph-50Hz * snaga: 1377 W * elektronska kontrola, integrisana | Type: MAGNA3 65-150 F (for hot water circulation in the circuit: desuperheater - hydraulic diverter for DHW): * water flow: 22100 l/h; * effortr: 100 kPa; * medium: technical water, 45/40°C; * Power supply: 220V-1ph-50Hz: * Power: 1377 W; * electronic control, integrated | kom/ pcs |  | 1 | 0
14. |  | Tip: MAGNA3 40-120 F (za cirkulaciju tople vode u krugu: hidraulična skretnica za STV - bojleri) * protok vode: 11200 l/h * napor: 80 kPa * medij: tehnička voda, 45/40°C * napajanje: 220V-1ph-50Hz * snaga: 427 W * elektronska kontrola, integrisana | Type: MAGNA3 40-120 F (for hot water circulation in the circuit: hydraulic switch for STV - boilers): * water flow: 11200 l/h; * effort: 80 kPa; * medium: technical water, 45/40°C; * power supply: 220V-1ph-50Hz; * Power: 427 W; * electronic control, integrated | kom/ pcs |  | 1 | 0
15. |  | Tip: UPS 32-100 N 180 (za recirkulaciju sanitarne tople vode) * protok vode: 1000 l/h * napor: 80 kPa * medij: sanitarna topla voda, 55°C * napajanje: 220V-1ph-50Hz * snaga: 345 W | Type: UPS 32-100 N 180 (for sanitary hot water recirculation): * water flow: 1000 l/h; * effort: 80 kPa; * medium: sanitary hot water, 55°C; * power supply: 220V-1ph-50Hz; * power: 345 W; | kom/ pcs |  | 1 | 0
|  | Isporuka i montaža membranskih ekspanzionih sudova proizvođača "Elbi" ili sl, u kompletu sa ventilom sigurnosti, sledećih tipova i količina: | Delivery and installation of membrane expansion tanks manufactured by "Elbi" or similar, complete with safety valve, of the following types and quantities:
16. |  | Tip ERCE 500, zapremine 500 l, dimenzije ∅775x1400 mm, priključak R5/4", sa ventilom sigurnosti R5/4" i pritiskom otvaranja 6 bar-a. | Type ERCE 500, volume 500 l, dimensions ∅775x1400 mm, connection R5/4", with safety valve R5/4" and opening pressure 6 bar. | komplet/ set |  | 1 | 0
17. |  | Tip ERCE 100, zapremine 100 l, dimenzije ∅500x775 mm, priključak 3/4", sa ventilom sigurnosti R3/4" i pritiskom otvaranja 6 bar-a. | Type ERCE 100, volume 100 l, dimensions ∅500x775 mm, connection 3/4", with safety valve R3/4" and opening pressure 6 bar. | kom/ pcs |  | 1 | 0
18. |  | Tip DV 200 CE (za sanitarnu toplu vodu), zapremine 200 l, dimenzije ∅600x1075 mm, priključak 5/4", sa ventilom sigurnosti R5/4" i pritiskom otvaranja 8 bar-a. | Type DV 200 CE (for sanitary hot water), volume 200 l, dimensions ∅600x1075 mm, connection 5/4", with safety valve R5/4" and opening pressure 8 bar. | kom/ pcs |  | 1 | 0
19. |  | Isporuka i montaža loptastih ventila sa leptirom ili ručicom, NP16, tip Glkobo H, proizvođač "IMI Hydronics Engineering" ili sl, sledećih dimenzija i količina: | Delivery and installation of ball valves with butterfly or handle, NP16, type Glkobo H, manufacturer "IMI Hydronics Engineering" or similar, with the following dimensions and quantities:
|  | R1/2" | R1/2" | kom/ pcs |  | 14 | 0
|  | R1" | R1" | kom/ pcs |  | 13 | 0
|  | R2" | R2" | kom/ pcs |  | 9 | 0
20. |  | Isporuka i montaža leptir ventila NP16, tip TA XUROX, proizvođača "IMI Hydronics Engineering" ili sl, sledećih dimenzija i količina: | Delivery and installation of butterfly valve NP16, type TA XUROX, manufactured by "IMI Hydronics Engineering" or similar, with the following dimensions and quantities:
|  | DN65 | DN65 | kom/ pcs |  | 3 | 0
|  | DN80 | DN80 | kom/ pcs |  | 7 | 0
|  | DN150 | DN150 | kom/ pcs |  | 12 | 0
|  | DN200 | DN200 | kom/ pcs |  | 5 | 0
21. |  | Isporuka i montaža pritisno nezavisnog regulacionog i balansnog ventila proizvođača "IMI Hydronics Engineering" ili sl, sledećih tipova, dimenzija i količina: | Delivery and installation of pressure-independent regulating and balancing valves manufactured by "IMI Hydronics Engineering" or similar of the following types, dimensions and quantities:
|  | TA MODULATOR 20 sa pokretačem TA-Slider 160 | TA MODULATOR 20 with actuator TA-Slider 160 | kom/ pcs |  | 2 | 0
|  | TA MODULATOR 40 sa pokretačem TA-Slider 500 | TA MODULATOR 40 with actuator TA-Slider 500 | kom/ pcs |  | 2 | 0
22. |  | Isporuka i montaža navojnog nepovratnog ventila, NP6, sledećih dimenzija i količina: | Delivery and installation of a threaded non-return valve, NP6, of the following dimensions and quantities:
|  | R1" | R1" | kom/ pcs |  | 2 | 0
|  | R2" | R2" | kom/ pcs |  | 3 | 0
23. |  | Isporuka i montaža međuprirubničkog nepovratnog ventila sa dvojnim diskom, tip GENEBRE 2401, proizvođača "IMI Hydronics Engineering" ili sl, NP16, sledećih dimenzija i količina: DN150 | Delivery and installation of an inter-flange non-return valve with a double disk, type GENEBRE 2401, manufactured by "IMI Hydronics Engineering" or similar, NP16, with the following dimensions and quantities: DN150 | kom/ pcs |  | 2 | 0
24. |  | Isporuka i montaža navojnog hvatača nečistoće, tip GENEBRE 3302, proizvođača "IMI Hydronics Engineering" ili sl, sledećih dimenzija i količina: R2" | Delivery and installation of a threaded dirt catcher, type GENEBRE 3302, manufactured by "IMI Hydronics Engineering" or similar, with the following dimensions and quantities: R2" | kom/ pcs |  | 1 | 0
25. |  | Isporuka i montaža prirubničkog hvatača nečistoće, NP16, sledećih dimenzija i količina: | Delivery and installation of a flanged dirt catcher, NP16, with the following dimensions and quantities:
|  | DN65 | DN65 | kom/ pcs |  | 1 | 0
|  | DN80 | DN80 | kom/ pcs |  | 2 | 0
|  | DN150 | DN150 | kom/ pcs |  | 1 | 0
|  | DN200 | DN200 | kom/ pcs |  | 1 | 0
26. |  | Isporuka i montaža prirubničkih gumenih kompenzatora, NP16, sledećih dimenzija i količina: | Delivery and installation of flanged rubber compensators, NP16, of the following dimensions and quantities:
|  | DN65 | DN65 | kom/ pcs |  | 2 | 0
|  | DN80 | DN80 | kom/ pcs |  | 4 | 0
|  | DN150 | DN150 | kom/ pcs |  | 6 | 0
27. |  | Isporuka i montaža mjerne blende, tipa MDFO, NP16, proizvođača "IMI Hydronics Engineering" ili sl, sledećih dimenzija i količina: | Delivery and installation of a measuring diaphragm, type MDFO, NP16, manufactured by "IMI Hydronics Engineering" or similar, with the following dimensions and quantities:
|  | DN80 | DN80 | kom/ pcs |  | 1 | 0
|  | DN150 | DN150 | kom/ pcs |  | 1 | 0
28. |  | Isporuka i montaža reducira pritiska sa manometrom, za sanitarnu hladnu vodu, sledećih dimenzija i količina: R2" | Delivery and installation of pressure reducers with manometer, for sanitary cold water, of the following dimensions and quantities: | kom/ pcs |  | 1 | 0
29. |  | Isporuka i montaža slavine za punjenje i pražnjenje sistema, R1/2", sa zaštitnom kapom i lančićem | Delivery and installation of the tap for filling and emptying the system, R1/2", with the protective cap and chain | kom/ pcs |  | 20 | 0
30. |  | Isporuka i montaža ručne ozračne slavine, R 3/8" | Delivery and installation of manual tap for air-releasing, R 3/8" | kom/ pcs |  | 20 | 0
31. |  | Isporuka i montaža automatskog ozračnog lončeta, R 1/2" | Delivery and installation of the automatic air-releasing pot, R 1/2" | kom/ pcs |  | 10 | 0
32. |  | Isporuka i montaža okruglog radijalnog manometra Ø80, mjernog opsega 0-10 ba: | Delivery and installation of the round radial manometer Ø80, measuring range 0-10 ba: | kom/ pcs |  | 10 | 0
33. |  | Isporuka i montaža manometarske slavine R1/2": | Delivery and installation of tap R1/2" for manometer: | kom/ pcs |  | 3 | 0
34. |  | Isporuka i montaža okruglog aksijalnog termometra Ø80, mjernog opsega 0-60C: | Delivery and installation of the round axial thermometer Ø80, measuring range 0-60OC: | kom/ pcs |  | 14 | 0
35. |  | Isporuka i montaža termostatskog mješnog ventila tip TA-MATIC, proizvođača "IMI Hydronics Engineering" ili sl,, DN50: | Delivery and installation of thermostatic mixing valve type TA-MATIC, manufactured by "IMI Hydronics Engineering" or similar, DN50: | kom/ pcs |  | 1 | 0
36. |  | Isporuka i montaža čeličnih bešavnih cijevi sa oblicima i mjerama prema DIN 2448 odnosno MEST EN 10220; sa tehničkim uslovima za isporuku prema DIN 1629 odnosno MEST EN 10216-1, kvalitet materijala P235TR1 ili viši, za izradu cijevne mreže sledećih dimenzija i količina: | Delivery and installation of seamless steel pipes with shapes and dimensions according to DIN 2448 or MEST EN 10220, with technical conditions for delivery according to DIN 1629 or MEST EN 10216-1, material quality P235TR1 or higher, for the production of a pipeline of the following dimensions and quantities:
|  | NO25 (Ø33,7x2,6 mm) | NO25 (Ø33,7x2,6 mm) | m1 |  | 24 | 0
|  | NO32 (Ø42,4x2,6 mm) | NO32 (Ø42,4x2,6 mm) | m1 |  | 18 | 0
|  | NO50 (Ø60,3x2,9 mm) | NO50 (Ø60,3x2,9 mm) | m1 |  | 30 | 0
|  | NO65 (Ø76,1x2,9 mm) | NO65 (Ø76,1x2,9 mm) | m1 |  | 24 | 0
|  | NO80 (Ø88,9x3,2 mm) | NO80 (Ø88,9x3,2 mm) | m1 |  | 16 | 0
|  | NO150 (Ø168,3x4,5 mm) | NO150 (Ø168,3x4,5 mm) | m1 |  | 12 | 0
|  | NO200 (Ø219,1x5,9 mm) | NO200 (Ø219,1x5,9 mm) | m1 |  | 12 | 0
37. |  | Za spojni i zaptivni materijal, elektrode za varenje, kiseonik i acetilen, hamburške lukove, redukcije, prelazne komade, razni fiting, ovjesni materijal (navojne šipke, cijevne obujmice, metalne čaure...), izradu čvrstih i kliznih oslonaca i sl, uzima se 50% od prethodne pozicije. | For connecting and sealing material, electrodes for welding, oxygen and acetylene, Hamburg arcs, reductions, transitional pieces, various fittings, suspension material (threaded rods, pipe clamps, metal bushings...), production of solid and sliding supports, etc., take is 50% of the previous position. |  |  | 0.5 | 0
38. |  | Čišćenje cijevne mreže i bojenje osnovnom bojom u dva premaza (nakon hidrauličke probe): | Cleaning of the pipe network and painting with the base colour in two coats (after the hydraulic test):
|  | Za cijevi zaključno sa NO50 | For pipes up to and including NO50 | m1 |  | 72 | 0
|  | Za cijevi preko NO50 | For pipes over NO50 | m2 |  | 24 | 0
|  | Ca cijevi DN65 i veće posebno se obračunava fiting: | For pipes DN65 and more extensive, the fitting is calculated separately:
39. |  | Hamburški lukovi za crne cijevi: | Hamburg arcs for black pipes:
|  | DN80 | DN80 | kom/ pcs |  | 16 | 0
|  | DN150 | DN150 | kom/ pcs |  | 18 | 0
|  | DN200 | DN200 | kom/ pcs |  | 16 | 0
40. |  | T-komadi za crne cijevi | T-pieces for black pipes:
|  | DN150 | DN150 | kom/ pcs |  | 2 | 0
|  | DN200 | DN200 | kom/ pcs |  | 2 | 0
41. |  | Redukcije za crne cijevi: | Reductions for black pipes:
|  | DN200/DN150 | DN200/DN150 | kom/ pcs |  | 2 | 0
|  | DN150/DN125 | DN150/DN125 | kom/ pcs |  | 2 | 0
|  | DN150/DN100 | DN150/DN100 | kom/ pcs |  | 2 | 0
|  | DN80/DN65 | DN80/DN65 | kom/ pcs |  | 2 | 0
|  | DN65/DN50 | DN65/DN50 | kom/ pcs |  | 2 | 0
|  | DN65/DN40 | DN65/DN40 | kom/ pcs |  | 2 | 0
42. |  | Izrada, isporuka i montaža razdjelnika i sabirnika DN250, dužine 1200 mm, sa priključcima 2XDN150 i 1xDN200 (izolacija obračunata posebno): | Producing, delivery and assembly of DN250 distributor and collector, length 1200 mm, with 2XDN150 and 1xDN200 connections (insulation calculated separately): | komplet/ set |  | 2 | 0
43. |  | Izrada, isporuka i montaža ozračnih lonaca sa prelivnom cijevi dužine do 6m i i ventilom R1/2", sledećih dimenzija i količina: | Producing, delivery and installation of pots for air-releasing with an overflow tube up to 6m long and an R1/2" valve, with the following dimensions and quantities:
|  | Ø139,7 mm; H=200 mm | Ø139,7 mm; H=200 mm | kom/ pcs |  | 4 | 0
|  | Ø273,0 mm; H=400 mm | Ø273,0 mm; H=400 mm | kom/ pcs |  | 4 | 0
44. |  | Isporuka i montaža PP-R cijevi za spajanje tople i hladne potrošne vode i recirkulacije sa bojlerima, tip FUSIOTHERM FASER, proizvođač "AQUATHERM" ili sl, sledećih dimenzija i količina: | Delivery and installation of PP-R pipes for connecting hot and cold consumption water and recirculation with boilers, type FUSIOTHERM FASER, manufacturer "AQUATHERM" or similar, of the following dimensions and quantities:
|  | DN50 (Ø63x8,6 mm) | DN50 (Ø63x8,6 mm) | m1 |  | 32 | 0
|  | DN25 (Ø32x4,4 mm) | DN25 (Ø32x4,4 mm) | m1 |  | 20 | 0
45. |  | Za spojni i zaptivni materijal, PP-R fiting (lukove, redukcije, prelazne komade...), ovjesni materijal (navojne šipke, cijevne obujmice, metalne čaure...) i sl. uzima se 50% od pozicije 31: | For connecting and sealing material, PP-R fitting (arcs, reductions, transition pieces...), suspension material (threaded bars, pipe clamps, metal bushings...) and similar. 50% of position 31 is taken: |  |  | 0.5 | 0
46. |  | Isporuka i montaža termičke izolacije sa strukturnom parnom branom za izolovanje cjevovoda tople i hladne vode (m≥7000), samogasive, na bazi sintetičkog kaučuka, tip ACE proizvođača "Armacell" ili sl. Sve uzdužne i sučeone spojeve spojiti lijepkom i po potrebi izolacionom trakom 50x3 mm. Izolacija je sledećih dimenzija i količina: | Delivery and installation of thermal insulation with a structural vapour barrier for insulating hot and cold water pipelines (m≥7000), self-extinguishing, based on synthetic rubber, type ACE manufactured by "Armacell" or similar. Connect all longitudinal and facing joints with adhesive and, if necessary, insulating tape 50x3 mm. The insulation has the following dimensions and quantities:
|  | cijevna izolacija Ø35x13 mm | pipe insulation Ø35x13 mm | m1 |  | 24 | 0
|  | cijevna izolacija Ø42x13 mm | pipe insulation Ø42x13 mm | m1 |  | 18 | 0
|  | cijevna izolacija Ø60x19 mm | pipe insulation Ø60x19 mm | m1 |  | 30 | 0
|  | cijevna izolacija Ø76x19 mm | pipe insulation Ø76x19 mm | m1 |  | 24 | 0
|  | cijevna izolacija Ø89x19 mm | pipe insulation Ø89x19 mm | m1 |  | 16 | 0
|  | ploča debljine 25 mm, bez samoljepljivog sloja (za cijevi DN100 i veće): | 25 mm thick plate, without self-adhesive layer (for pipes DN100 and larger): | m2 |  | 25 | 0
|  | ploča debljine 32 mm, za izolovanje akumulacionih sudova: | 32 mm thick plate for insulating storage tanks: | m2 |  | 22 | 0
47. |  | Dodatna izolacija cjevovoda i armature u dvorištu objekta kaučukom debljine 32 mm u oblozi od aluminijskog lima debljine 0,5 mm: | Additional insulation of pipelines and fittings in the yard of the facility with 32 mm thick rubber in the 0.5 mm thick aluminium sheet lining: | m2 |  | 30 | 0
48. |  | Izrada, isporuka i montaža konstrukcije od profilnog gvožđa i nosača za nošenje cjevovoda i opreme | Production, delivery and installation of structures made of profiled iron and supports for fixing pipelines and equipment | kg |  | 400 | 0
I. |  | TOPLOTNA PUMPA I PODSTANICA ZA GRIJANJE I HLAĐENJE ŠKOLE | HEAT PUMP AND SUBSTATION FOR HEATING AND COOLING OF THE SCHOOL |  |  | Ukupno/ Total | 0
II. |  | INSTALACIJA VENTILATOR-KONVEKTORA | FAN-CONVECTOR INSTALLATION
|  | Isporuka i montaža kasetnih dvocijevnih ventilator-konvektora (fan-coil aparata) sa maskom i Modbus karticom za upravljanje, proizvođača "CLIVET" - Italija ili sl; sledećih tipova, karakteristika i količina: | Delivery and installation of cassette two-pipe fan coil units (fan-coil apparatus) with mask and Modbus control card, manufactured by "CLIVET" - Italy or similar, of the following types, characteristics and quantities:
49. |  | Tip: CFK 007.0 CC2 rashladni medijum: voda 7/12C grejni medijum: voda 45/40C rashladni kapacitet senzibilni: 1590 W rashladni kapacitet ukupni: 2350 W grejni kapacitet: 2490 W protok vazduha: 392 m3/h protok vode: 405 l/h pad pritiska vodnog izmjenjivača: 5,97 kPa nivo zvučnog pritiska na srednjoj brzini: 29 dB(A) napajanje: 230V-1ph-50Hz električna snaga: 22,7 W dimenzije (WxDxH): 650x650x213 mm masa: 22,5 kg | Type: CFK 007.0 CC2: cooling medium: water 7/12°C; heating medium: water 45/40°C; cooling capacity sensitive: 1590 W; total cooling capacity: 2350 W; heating capacity: 2490 W; air flow: 392 m3/h; water flow: 405 l/h; water exchanger pressure drop: 5.97 kPa; sound pressure level at medium speed: 29 dB(A); power supply: 230V-1ph-50Hz; electrical power: 22.7 W; dimensions (WxDxH): 650x650x213 mm; mass: 22.5 kg | kom/ pcs |  | 5 | 0
50. |  | Tip: CFK 011.0 CC2 rashladni medijum: voda 7/12C grejni medijum: voda 45/40C rashladni kapacitet senzibilni: 2110 W rashladni kapacitet ukupni: 3090 W grejni kapacitet: 3280 W protok vazduha: 502 m3/h protok vode: 532 l/h pad pritiska vodnog izmjenjivača: 8,06 kPa nivo zvučnog pritiska na srednjoj brzini: 36 dB(A) napajanje: 230V-1ph-50Hz električna snaga: 27 W dimenzije (WxDxH): 650x650x213 mm masa: 22,5 kg | Type: CFK 011.0 CC2: cooling medium: water 7/12°C; heating medium: water 45/40°C; cooling capacity sensitive: 2110 W; total cooling capacity: 3090 W; heating capacity: 3280 W; air flow:502 m3/h; water flow:532 l/h; water exchanger pressure drop: 8.06 kPa; sound pressure level at medium speed: 36 dB(A); power supply: 230V-1ph-50Hz; electrical power: 27 W; dimensions (WxDxH): 650x650x213 mm; mass: 22.5 kg | kom/ pcs |  | 7 | 0
51. |  | Tip: CFK 021.0 CC2 rashladni medijum: voda 7/12C grejni medijum: voda 45/40C rashladni kapacitet senzibilni: 3110 W rashladni kapacitet ukupni: 4490 W grejni kapacitet: 4910 W protok vazduha: 793 m3/h protok vode: 773 l/h pad pritiska vodnog izmjenjivača: 18,3 kPa nivo zvučnog pritiska na srednjoj brzini: 33 dB(A) napajanje: 230V-1ph-50Hz električna snaga: 42 W dimenzije (WxDxH): 950x950x213 mm masa: 28 kg | Type: CFK 021.0 CC2 : cooling medium: water 7/12°C; heating medium: water 45/40°C; cooling capacity sensitive: 3110 W; total cooling capacity: 4490 W; heating capacity: 4910 W; air flow: 793 m3/h; water flow:773 l/h; water exchanger pressure drop:18.3 kPa; sound pressure level at medium speed: 33 dB(A); power supply: 230V-1ph-50Hz; electrical power: 42 W; dimensions (WxDxH): 950x950x213 mm; mass: 28 kg | kom/ pcs |  | 24 | 0
52. |  | Tip: CFK 031.0 CC2 rashladni medijum: voda 7/12C grejni medijum: voda 45/40C rashladni kapacitet senzibilni: 3880 W rashladni kapacitet ukupni: 5620 W grejni kapacitet: 6100 W protok vazduha: 1117 m3/h protok vode: 967 l/h pad pritiska vodnog izmjenjivača: 16,34 kPa nivo zvučnog pritiska na srednjoj brzini: 39 dB(A) napajanje: 230V-1ph-50Hz električna snaga: 90 W dimenzije (WxDxH): 950x950x213 mm masa: 33 kg | Type: CFK 031.0 CC2 : cooling medium: water 7/12°C; heating medium: water 45/40°C; cooling capacity sensitive: 3880 W; total cooling capacity:5620 W; heating capacity: 6100 W; air flow:1117 m3/h; water flow 967 l/h; water exchanger pressure drop:16.34 kPa; sound pressure level at medium speed: 39 dB(A); power supply: 230V-1ph-50Hz; electrical power: 90 W; dimensions (WxDxH): 950x950x213 mm; mass: 33 kg | kom/ pcs |  | 38 | 0
53. |  | Tip: CFK 041.0 CC2 rashladni medijum: voda 7/12OC grejni medijum: voda 45/40OC rashladni kapacitet senzibilni: 5670 W rashladni kapacitet ukupni: 8310 W grejni kapacitet: 8760 W protok vazduha: 1295 m3/h protok vode: 1430 l/h pad pritiska vodnog izmjenjivača: 25,29 kPa nivo zvučnog pritiska na srednjoj brzini: 40 dB(A) napajanje: 230V-1ph-50Hz električna snaga: 124 W dimenzije (WxDxH): 950x950x213 mm masa: 34,5 kg | Type: CFK 041.0 CC2 : cooling medium: water 7/12°C; heating medium: water 45/40°C; cooling capacity sensitive: 5670 W; total cooling capacity: 8310 W; heating capacity:8760 W; air flow:1295 m3/h; water flow: 1430 l/h; water exchanger pressure drop: 25.29 kPa; sound pressure level at medium speed: 40 dB(A); power supply: 230V-1ph-50Hz; electrical power: 124 W; dimensions (WxDxH): 950x950x213 mm; mass: 34.5 kg | kom/ pcs |  | 42 | 0
54. |  | Individualni zidni kontroler za ugradnju u kabinetima, tip PEMC00003 - KJR90X | Individual wall controller for installation in cabinets, type PEMC00003 - KJR90X | kom/ pcs |  | 18 | 0
55. |  | Isporuka i montaža crnih čeličnih cijevi po MEST EN 10220:2002 (zaključno sa dimenzijom NO50 srednje teške navojne, za dimenzije veće od NO50 bešavne), sledećih dimenzija i količina: | Delivery and installation of black steel pipes according to MEST EN 10220:2002 (including dimension NO50 medium heavy threaded, for sizes greater than NO50 seamless) of the following sizes and quantities:
|  | NO20 (Ø26,9x2,65 mm) | NO20 (Ø26,9x2,65 mm) | m1 |  | 110 | 0
|  | NO25 (Ø33,7x3,25 mm) | NO25 (Ø33,7x3,25 mm) | m1 |  | 486 | 0
|  | NO32 (Ø42,4x3,25 mm) | NO32 (Ø42,4x3,25 mm) | m1 |  | 606 | 0
|  | NO40 (Ø48,3x3,25 mm) | NO40 (Ø48,3x3,25 mm) | m1 |  | 186 | 0
|  | NO50 (Ø60,3x3,65 mm) | NO50 (Ø60,3x3,65 mm) | m1 |  | 162 | 0
|  | NO65 (Ø76,1x2,90 mm) | NO65 (Ø76,1x2,90 mm) | m1 |  | 174 | 0
|  | NO80 (Ø88,9x3,20 mm) | NO80 (Ø88,9x3,20 mm) | m1 |  | 150 | 0
|  | NO100 (Ø114,3x3,60 mm) | NO100 (Ø114,3x3,60 mm) | m1 |  | 200 | 0
|  | NO125 (Ø139,7x4,00 mm) | NO125 (Ø139,7x4,00 mm) | m1 |  | 75 | 0
|  | NO150 (Ø168,3x4,50 mm) | NO150 (Ø168,3x4,50 mm) | m1 |  | 50 | 0
|  | NO200 (Ø219.1x5,9 mm) | NO200 (Ø219.1x5,9 mm) | m1 |  | 55 | 0
56. |  | Za spojni i zaptivni materijal, elektrode za varenje, kiseonik i acetilen, hamburške lukove, redukcije, prelazne komade, razni fiting, ovjesni materijal (navojne šipke, cijevne obujmice, metalne čaure...), izradu čvrstih i kliznih oslonaca i sl, uzima se 50% od prethodne pozicije. | For connecting and sealing material, electrodes for welding, oxygen and acetylene, Hamburg arcs, reductions, transitional pieces, various fittings, suspension material (threaded bars, pipe clamps, metal bushings...), producing of solid and sliding supports, etc., 50% of the previous position is taken. |  |  | 0.5 | 0
57. |  | Čišćenje cijevne mreže i bojenje osnovnom bojom u dva premaza (nakon hidrauličke probe): | Cleaning of the pipe network and painting with the base colour in two coats (after the hydraulic test):
|  | Za cijevi zaključno sa NO50 | For pipes up to and including NO50 | m1 |  | 1550 | 0
|  | Za cijevi preko NO50 | For pipes over NO50 | m2 |  | 164 | 0
|  | Za cijevi DN65 i veće posebno se obračunava fiting: | Fittings are calculated separately for pipes DN65 and larger:
58. |  | Hamburški lukovi za crne cijevi | Hamburg arcs for black pipes
|  | DN100 | DN100 | kom/ pcs |  | 4 | 0
|  | DN125 | DN125 | kom/ pcs |  | 4 | 0
|  | DN150 | DN150 | kom/ pcs |  | 6 | 0
|  | DN200 | DN200 | kom/ pcs |  | 16 | 0
59. |  | T-komadi za crne cijevi | T-pieces for black pipes:
|  | DN80 | DN80 | kom/ pcs |  | 4 | 0
|  | DN100 | DN100 | kom/ pcs |  | 6 | 0
|  | DN125 | DN125 | kom/ pcs |  | 4 | 0
|  | DN150 | DN150 | kom/ pcs |  | 4 | 0
|  | DN200 | DN200 | kom/ pcs |  | 4 | 0
60. |  | T-komadi za crne cijevi | T-pieces for black pipes:
|  | DN200/DN150 | DN200/DN150 | kom/ pcs |  | 2 | 0
|  | DN200/DN100 | DN200/DN100 | kom/ pcs |  | 2 | 0
|  | DN150/DN125 | DN150/DN125 | kom/ pcs |  | 2 | 0
|  | DN125/DN100 | DN125/DN100 | kom/ pcs |  | 10 | 0
|  | DN100/DN80 | DN100/DN80 | kom/ pcs |  | 10 | 0
|  | DN100/DN65 | DN100/DN65 | kom/ pcs |  | 4 | 0
|  | DN100/DN50 | DN100/DN50 | kom/ pcs |  | 2 | 0
|  | DN80/DN65 | DN80/DN65 | kom/ pcs |  | 8 | 0
|  | DN80/DN50 | DN80/DN50 | kom/ pcs |  | 2 | 0
|  | DN80/DN40 | DN80/DN40 | kom/ pcs |  | 2 | 0
|  | DN65/DN50 | DN65/DN50 | kom/ pcs |  | 12 | 0
61. |  | Izrada, isporuka i montaža ozračnih lonaca sa prelivnom cijevi dužine do 6m i i ventilom R1/2", sledećih dimenzija i količina: Ø219,1 mm; L=400 mm | Producing, delivery and installation of pots for air-releasing, with the overflow tube up to 6m long and the R1/2" valve, with the following dimensions and quantities: Ø219,1 mm; L=400 mm | komplet/ set |  | 2 | 0
62. |  | Isporuka i montaža cijevnih veza od višeslojnih PEx-Al-PEx cijevi, za spajanje ventilator-konvektora sa cjevovodom, komplet sa kompresionim poluspojnicama na oba kraja, sledećih dimenzija i količina: | Delivery and installation of pipe connections made of multilayer PEx-Al-PEx pipes for connecting the fan-coiler to the pipeline, complete with compression semi-couplers on both ends, with the following dimensions and quantities:
|  | Ø20x2mm - 3/4", L=1m | Ø20x2mm - 3/4", L=1m | komplet/ set |  | 108 | 0
|  | Ø26x3mm - 1", L=1m | Ø26x3mm - 1", L=1m | komplet/ set |  | 114 | 0
|  | Ø32x3mm - 1", L=1m | Ø32x3mm - 1", L=1m | komplet/ set |  | 126 | 0
63. |  | Isporuka i montaža PVC cijevi za izradu kondenz-mreže, sledećih dimenzija i količina: | Delivery and installation of PVC pipes for the condensation pipeline, of the following dimensions and quantities:
|  | Ø32mm | Ø32mm | m1 |  | 1100 | 0
|  | Ø50mm | Ø50mm | m1 |  | 526 | 0
64. |  | Za PP fiting (lukovi, redukcije, T-komadi, spojnice i sl.) kao i za ovjesni materijal (navojne šipke, cijevne obujmice, metalne čaure i sl.) uzima se 50% od prethodne pozicije: | For PP fittings (arcs, reductions, T-pieces, couplings, etc.) and suspension material (threaded rods, pipe clamps, metal bushings, etc.), 50% of the previous position is taken: | komplet |  | 0.5 | 0
65. |  | Isporuka i montaža termičke izolacije sa strukturnom parnom branom za izolovanje cjevovoda tople i hladne vode (m≥7000), samogasive, na bazi sintetičkog kaučuka, tip ACE proizvođača "Armacell" ili sl. Sve uzdužne i sučeone spojeve spojiti lijepkom i po potrebi izolacionom trakom 50x3 mm. Izolacija je sledećih dimenzija i količina: | Delivery and installation of thermal insulation with a structural vapour barrier for insulating hot and cold water pipelines (μ≥7000), self-extinguishing, based on synthetic rubber, type ACE manufactured by "Armacell" or similar. Connect all longitudinal and facing joints with adhesive and, if necessary, insulating tape 50x3 mm. The insulation has the following dimensions and quantities:
|  | * Za cijevne veze: | * For pipe connections:
|  | cijevna izolacija Ø22x9 mm | pipe insulation Ø22x9 mm | m1 |  | 108 | 0
|  | cijevna izolacija Ø28x13 mm | pipe insulation Ø28x13 mm | m1 |  | 114 | 0
|  | cijevna izolacija Ø35x13 mm | pipe insulation Ø35x13 mm | m1 |  | 126 | 0
|  | * Za crne cijevi: | * For black pipes:
|  | cijevna izolacija Ø28x13 mm | pipe insulation Ø28x13 mm | m1 |  | 110 | 0
|  | cijevna izolacija Ø35x13 mm | pipe insulation Ø35x13 mm | m1 |  | 486 | 0
|  | cijevna izolacija Ø42x13 mm | pipe insulation Ø42x13 mm | m1 |  | 606 | 0
|  | cijevna izolacija Ø48x13 mm | pipe insulation Ø48x13 mm | m1 |  | 186 | 0
|  | cijevna izolacija Ø60x19 mm | pipe insulation Ø60x19 mm | m1 |  | 162 | 0
|  | cijevna izolacija Ø76x19 mm | pipe insulation Ø76x19 mm | m1 |  | 174 | 0
|  | cijevna izolacija Ø89x19 mm | pipe insulation Ø89x19 mm | m1 |  | 150 | 0
|  | ploča debljine 25 mm, bez samoljepljivog sloja (za cijevi DN100 i veće): | 25 mm thick plate, without self-adhesive layer (for pipes DN100 and larger): | m2 |  | 175 | 0
66. |  | Isporuka i montaža loptastih ventila sa leptirom ili ručicom, NP16, tip Glkobo H, proizvođač "IMI Hydronics Engineering" ili sl, sledećih dimenzija i količina: | Delivery and installation of ball valves with butterfly or handle, NP16, type Glkobo H, manufacturer "IMI Hydronics Engineering" or similar, with the following dimensions and quantities:
|  | R3/4" | R3/4" | kom/ pcs |  | 24 | 0
|  | R1" | R1" | kom/ pcs |  | 124 | 0
|  | R5/4" | R5/4" | kom/ pcs |  | 84 | 0
|  | R2" | R2" | kom/ pcs |  | 2 | 0
67. |  | Isporuka i montaža leptir ventila NP16, tip TA XUROX, proizvođača "IMI Hydronics Engineering" ili sl, sledećih dimenzija i količina: | Delivery and installation of butterfly valve NP16, type TA XUROX, manufactured by "IMI Hydronics Engineering" or similar, with the following dimensions and quantities:
|  | DN125 | DN125 | kom/ pcs |  | 2 | 0
|  | DN150 | DN150 | kom/ pcs |  | 2 | 0
68. |  | Isporuka i montaža prestrujnih ventila, tip HIDROLUX, proizvođača "IMI Hydronics Engineering" ili sl, sledećih dimenzija i količina: DN20 | Delivery and installation of HYDROLUX type differential pressure overflow valves, manufactured by "IMI Hidronics Engineering" or similar, of the following dimensions and quantities: DN 20. | kom/ pcs |  | 10 | 0
69. |  | Isporuka i montaža pritisno nezavisnog regulacionog i balansnog ventila za montažu na priključku ventilator - konvektora, tip TA-COMPACT-P sa aktuatorom EMO T, proizvođača "IMI Hydronics Engineering" ili sl, sledećih dimenzija i količina: | Delivery and installation of a pressure-independent regulating and balancing valve for installing on the fan-convector connection, type TA-COMPACT-P with actuator EMO T, manufactured by "IMI Hydronics Engineering" or similar, with the following dimensions and quantities:
|  | TA-COMPACT-P 15 | TA-COMPACT-P 15 | kom/ pcs |  | 12 | 0
|  | TA-COMPACT-P 20 | TA-COMPACT-P 20 | kom/ pcs |  | 62 | 0
|  | TA-COMPACT-P 25 | TA-COMPACT-P 25 | kom/ pcs |  | 42 | 0
70. |  | Isporuka i montaža slavine za punjenje i pražnjenje sistema, R1/2", sa zaštitnom kapom i lančićem | Delivery and installation of the tap for filling and emptying the system, R1/2", with protective cap and chain | kom/ pcs |  | 26 | 0
71. |  | Isporuka i montaža ručne ozračne slavine, R 3/8" | Delivery and installation of manual tap for air-releasing, R 3/8" | kom/ pcs |  | 26 | 0
72. |  | Isporuka i montaža automatskog ozračnog lončeta, R 1/2" | Delivery and installation of an automatic pot for air-releasing, R 1/2" | kom/ pcs |  | 26 | 0
73. |  | Isporuka i montaža gipsane revizije tipa Alu Star, proizvođača Knauf ili sl, sledećih dimenzija i količina: 400x400 mm | Delivery and installation of Alu Star type plaster revision, manufactured by Knauf or similar, of the following dimensions and quantities: 400x400mm. | kom/ pcs |  | 120 | 0
74. |  | Izrada, isporuka i montaža konstrukcije od profilnog gvožđa i nosača za nošenje cjevovoda: | Production, delivery and installation of the structure made of profiled iron and supports for pipelines: | kg |  | 200 | 0
II. |  | INSTALACIJA VENTILATOR-KONVEKTORA | FAN-CONVECTOR INSTALLATION |  |  | Ukupno/ Total | 0
III. |  | SOLARNA INSTALACIJA | SOLAR INSTALLATION
75. |  | Isporuka i montaža solarnih panelnih kolektora tipa Vitosol 100-FM sa selektivnim slojem ThermProtect, proizvođača "Viessmann" ili sl, sledećih karakteristika: Tip: SH1F Bruto površina: 2,51 m2 Površina apsorbera: 2,31 m2 Aperturna površina: 2,33 m2 Širina: 2.380 mm Visina: 1.056 mm Dubina: 73 mm Zapremina sredstva za prenos toplote: 2,4 l Dozvoljeni radni pritisak kolektora: 6 bar Optički stepen iskorišćenja (površina apsorbera): 81,4 % | Delivery and installation of solar panel collectors type Vitosol 100-FM with the selective ThermProtect layer, manufactured by "Viessmann" or similar, with the following characteristics: Type: SH1F; Gross area: 2.51 m2; Absorber surface: 2.31 m2; Aperture area: 2.33 m2; Width: 2,380 mm; Height: 1,056 mm; Depth: 73 mm; The volume of heat transfer medium: 2.4 l; Permitted operating pressure of the collector: 6 bar; Optical efficiency (absorber surface): 81.4%; | kom/ pcs |  | 20 | 0
76. |  | Isporuka i montaža spojnih cijevi (2 kom.) za solarne kolektore, proizvođača "Viessmann" ili sl: | Delivery and installation of connecting pipes (2 pcs.) for solar collectors manufactured by "Viessmann" or similar: | komplet/ set |  | 18 | 0
77. |  | Priključak - set jednostran, proizvođača "Viessmann" ili sl: | Connection - one-sided set, manufactured by "Viessmann" or similar: | kom/ pcs |  | 2 | 0
78. |  | Set uronskih čaura za solarni sistem, proizvođača "Viessmann" ili sl: | The set of immersion sleeves for the solar system, manufactured by "Viessmann" or similar: | komplet/ set |  | 1 | 0
79. |  | Učvršćenje ravnih kolektora vodoravno, proizvođača "Viessmann" ili sl: | Fixing flat collectors horizontally, manufactured by "Viessmann" or similar: | komplet/ set |  | 2 | 0
80. |  | Odvajač vazduha horizontalni 1 1/4" samozatvarajući, proizvođača "Viessmann" ili sl: | Air separator horizontal 1 1/4" self-closing, manufactured by "Viessmann" or similar: | kom/ pcs |  | 1 | 0
81. |  | Brzi odzračnik 3/8" Solar 6 bar 150°C, proizvođača "Viessmann" ili sl: | Quick air-releaser 3/8" Solar 6 bar 150°C, manufactured by "Viessmann" or similar: | kom/ pcs |  | 2 | 0
82. |  | Solarna pumpna grupa DN 25, sa integrisanom visokoefikasnom cirkulacionom pumpom sa PWM izlazom, mjeračem protoka, termometrima, manometrom, odvajačem vazduha, zapornom armaturom, ventilom sigurnosti, kompaktna, sa izolacijom. Raspoloživi napor 90kPa pri protoku 2000 l/h proizvođača "Viessmann" ili sl: | Solar pump group DN 25, with integrated high-efficiency circulation pump with PWM output, flow meter, thermometers, manometer, air separator, shut-off fitting, valve security, compact, and with insulation. Available effort 90kPa at a flow rate of 2000 l/h, manufacturer "Viessmann" or similar: | komplet/ set |  | 1 | 0
83. |  | Toplotni medijum Tyfocor LS Mediter. 25 l, tačka mržnjenja -12˚C, proizvođača "Viessmann" ili sl: | Thermal medium Tyfocor LS Mediter. 25 l, freezing point -12˚C, manufacturer "Viessmann" or similar: | komplet/ set |  | 15 | 0
84. |  | Solarna ekspanziona posuda sa ventilom za zatvaranje i nožicama za pričvršćivanje, zapremine 80 l, radni pritisak 10 bar-a, proizvođača "Viessmann" ili sl: | Solar expansion tank with shut-off valve and fixing feet, volume 80 l, working pressure 10 bar, manufactured by "Viessmann" or similar: | kom/ pcs |  | 2 | 0
85. |  | Elektronska regulacija diferencijalne temperature za instalacije sa do četiri potrošača, za bivalentne instalacije sa solarnim kolektorima i kotlovima na lako lož ulje/gas i čvrsto gorivo, tip Vitosolic 200 SD4, proizvođača "Viessmann" ili sl: | Electronic differential temperature regulation for installations with up to four consumers, for bivalent installations: with solar collectors and light fuel oil/gas boilers, and solid fuel, type Vitosolic 200 SD4, manufactured by "Viessmann" or similar: | komplet/ set |  | 1 | 0
86. |  | Uronski senzor temperature (NTC 10k) za ugradnju u bojler PTV, sa priključnim vodom dužine 3,7 m, proizvođača "Viessmann" ili sl: | Immersion temperature sensor (NTC 10k) for installation in the DHW boiler, with a 3.7 m long connection line, manufactured by "Viessmann" or similar: | kom/ pcs |  | 2 | 0
87. |  | Isporuka i montaža bakarnih polutvrdih cijevi u šipkama, sledećih dimenzija i količina: | Delivery and installation of semi-hard copper pipes in bars of the following dimensions and quantities:
|  | Ø28x1 mm | Ø28x1 mm | m1 |  | 20 | 0
|  | Ø35x1 mm | Ø35x1 mm | m1 |  | 205 | 0
88. |  | Za spojni i zaptivni materijal, elektrode za varenje, kiseonik i acetilen, bakarni fiting, ovjesni materijal (navojne šipke, cijevne obujmice, metalne čaure...), izradu čvrstih i kliznih oslonaca i sl, uzima se 50% od prethodne pozicije. | For connecting and sealing material, electrodes for welding, oxygen and acetylene, copper fitting, suspension material (threaded bars, pipe clamps, metal bushings...), production of solid and sliding supports, etc., 50% of the previous position is taken. |  |  | 0.5 | 0
89. |  | Isporuka i montaža termičke izolacije otporne na visoke temperature, za izolovanje cjevovoda tople vode, samogasive, na bazi sintetičkog kaučuka, tip HF proizvođača "Armacell" ili sl, sledećih dimenzija i količina: | Delivery and installation of thermal insulation resistant to high temperatures for insulating hot water pipelines, self-extinguishing, based on synthetic rubber, type HF manufactured by "Armacell" or similar, of the following dimensions and quantities:
|  | Ø28x19 mm | Ø28x19 mm | m1 |  | 20 | 0
|  | Ø35x19 mm | Ø35x19 mm | m1 |  | 205 | 0
90. |  | Dodatna izolacija cjevovoda na krovu objekta u oblozi od aluminijskog lima debljine 0,5 mm: | Additional insulation of pipelines on the roof of the building by the covering of aluminium sheet 0.5 mm thick | m2 |  | 10 | 0
III. |  | SOLARNA INSTALACIJA | SOLAR INSTALLATION |  |  | Ukupno | 0
IV. |  | VENTILACIJA ŠKOLE | VENTILATION OF SCHOOL
|  | Isporuka i montaža ventilatora proizvođača "Systemair" ili slično; sledećih tipova, karakteristika i količina: | Delivery and installation of fans manufactured by "Systemair" or similar; of the following types, characteristics and quantities:
91. |  | Krovni ventilator za odsis vazduha iz toaleta i garderoba (Sistem S-1i): tip: DVN 450EC protok: 1750 m3/h napor: 130 Pa električno napajanje: 380-3ph-50HZ-140.9W- 0,29A | Roof fan for air extraction from toilets and wardrobes (System S-1i): type: DVN 450EC; flow: 1750 m3/h; effort: 130 Pa; power supply: 380-3ph-50HZ-140.9W- 0.29A | komplet/ set |  | 1 | 0
92. |  | Krovni ventilator za odsis vazduha iz toaleta i garderoba (Sistem S-2i): proizvod: Systemair - Švedska ili sl, tip: DVN 355EC protok: 1550 m3/h napor: 130 Pa električno napajanje: 220V-1ph-50HZ-132.2W-0.6A | Roof fan for air extraction from toilets and wardrobes (System S-2i): product: Systemair - Sweden or similar, type: DVN 355EC; flow: 1550 m3/h; effort: 130 Pa; power supply: 220-1ph-50HZ-132.2W- 0.6A | komplet/ set |  | 1 | 0
93. |  | Okrugli kanalski ventilator svježeg vazduha za kancelarije (Sistem S-3u): proizvod: Systemair - Švedska ili sl, tip: prio 160EC circ. Duct fan protok: 200 m3/h napor: 50 Pa električno napajanje: 230V-1ph-50HZ-10.8W-0,19A dodatna oprema: regulator protoka: REE 1 | Round channel fresh air fan for offices (System S-3u): product: Systemair - Sweden or similar, type: prio 160EC circ. Duct fan flow rate: 200 m3/h; effort: 50 Pa; power supply: 230V-1ph-50HZ-10.8W-0.19A; additional equipment: flow regulator: REE 1 | komplet/ set |  | 1 | 0
94. |  | Okrugli kanalski ventilator odsis vazduha iz toaleta osoblja (Sistem S-3i): proizvod: Systemair - Švedska ili sl, tip: K 250 EC Sileo protok: 200 m3/h napor: 130 Pa električno napajanje: 230V-1ph-50HZ-22.6W-0,2A dodatna oprema: regulator protoka: REE 1 | Round channel fan exhausting air from the staff toilet (System S-3i): product: Systemair - Sweden or similar, type: K 250 EC Sileo; flow rate: 200 m3/h; effort: 130 Pa; power supply: 230V-1ph-50HZ-22.6W-0.2A; additional equipment: flow regulator: REE 1 | komplet/ set |  | 1 | 0
95. |  | Ventilator za nadpritisak liftovskog okna (Sistem NP1): tip: MUB 062 630D6 IE2 Multibox protok: 5705 m3/h napor: 200 Pa električno napajanje: 380-3ph-50HZ-1398.1W-3,4A dodatna oprema: * zaštita od kiše WSD 062 * žaluzina za usis vazduha WSG 062 * termička zaštita motora U-EK230E * frekventni regulator FXDM5AM | Elevator shaft overpressured fan (System NP1): type: MUB 062 630D6 IE2 Multibox; flow rate: 5705 m3/h; effort: 200 Pa; power supply: 380-3ph-50HZ-1398.1W-3.4A; Accessories: * rain protection WSD 062; * grilles for air intake WSG 062; * U-EK230E motor thermal protection; * frequency regulator FXDM5AM | komplet/ set |  | 1 | 0
96. |  | Isporuka i montaža dvostruke ventilacione jedinica sa rekuperatorom toplote za ventilaciju tehničkih prostorija u suterenu (Sistem S-5u/S-5i), sledećih karakteristika: proizvođač: "JAKKA" ili sl. tip: JRH73/5000 protok: 3500 m3/h napor: 175 Pa električno napajanje: 230V-1ph-50HZ-486W koeficijent povrata osjetne toplote: 51% dodatna oprema: kontroler "Jakka Control Kit 4" sa mogućnošću povezivanja na BMS. | Delivery and installation of double ventilation units with heat recuperator for ventilation of technical rooms in the basement (System S-5u/S-5i), with the following characteristics: Manufacturer: "JAKKA" or similar; type: JRH73/5000; flow: 3500 m3/h; effort: 175 Pa; electrical supply: 230V-1ph-50HZ-486W; sensible heat recovery coefficient: 51%; additional equipment: controller "Jakka Control Kit 4" with the possibility of connecting to BMS. | komplet/ set |  | 1 | 0
97. |  | Isporuka i montaža kanalskog električnog predgrijača na dovodu svježeg vazduha, komplet sa spoljašnjim senzorom temperature i automatikom za vođenje, sledećih karakteristika: Predgrijač sistema Rek proizvođač: "JAKKA" ili sl. snaga. 13,5 kW dimenzije: 450x400x410 mm dodatna oprema: kontroler "Jakka Control Kit 4" sa mogućnošću povezivanja na BMS, senzor temperature vazduha: | Delivery and installation of the channel electric preheater on the fresh air supply, complete with external temperature sensor and automatic control, with the following characteristics: System preheater Rek; manufacturer: "JAKKA" or similar; Power. 13.5 kW; dimensions: 450x400x410 mm; additional equipment: controller "Jakka Control Kit 4" with the possibility of connecting to BMS, air temperature sensor: | komplet/ set |  | 1 | 0
98. |  | Isporuka i montaža spoljne protivkišne žaluzine sa zaštitnom mrežicom, tip AFZV, proizvođač "Klimaoprema" ili slično, u RAL tonu prema zahtjevima arhitekture, sledećih dimenzija i količina: | Delivery and installation of external rain grilles with protective mesh, type AFZV, manufacturer "Klimaoprema" or similar, in RAL tone according to architectural requirements, with the following dimensions and quantities:
|  | 300x200 mm | 300x200 mm | kom/ pcs |  | 2 | 0
|  | 1000x800 mm | 1000x800 mm | kom/ pcs |  | 2 | 0
99. |  | Isporuka i montaža aluminijske rešetke za dovod vazduha sa dva reda pojedinačno podesivih lamela u kompletu sa regulatorom protoka i ugradnim ramom, tip OAH2-L-UR RAL 9010, proizvođača "Klimaoprema" ili slično, sledećih dimenzija i količina: | Delivery and installation of the aluminium grille for air supply with two rows of individually adjustable slats with the flow regulator and built-in frame, type OAH2-L-UR RAL 9010, manufactured by "Klimaoprema" or similar, with the following dimensions and quantities:
|  | 325x125 mm | 325x125 mm | kom/ pcs |  | 1 | 0
|  | 525x125 mm | 525x125 mm | kom/ pcs |  | 2 | 0
|  | 625x125 mm | 625x125 mm | kom/ pcs |  | 2 | 0
|  | 1025x125 mm | 1025x125 mm | kom/ pcs |  | 5 | 0
100. |  | Isporuka i montaža aluminijske rešetke za odvod vazduha sa nepomičnim kvadratnim saćem, u kompletu sa regulatorom protoka i ugradnim ramom, tip OAK-L-UR RAL 9010, proizvođača "Klimaoprema" ili slično, sledećih dimenzija i količina: | Delivery and installation of the aluminium grid for air drainage with a fixed square grid, the flow regulator and built-in frame, type OAK-L-UR RAL 9010, manufactured by "Klimaoprema" or similar, with the following dimensions and quantities:
|  | 325x125 mm | 325x125 mm | kom/ pcs |  | 1 | 0
|  | 525x125 mm | 525x125 mm | kom/ pcs |  | 2 | 0
|  | 625x125 mm | 625x125 mm | kom/ pcs |  | 2 | 0
|  | 1025x125 mm | 1025x125 mm | kom/ pcs |  | 5 | 0
101. |  | Isporuka i montaža aluminijske prestrujna rešetka sa jednim redom horizontalnih nepomičnih, neprovidnih lamela, u kompletu sa kontraramom za ugradnju na vrata, tip OASR, proizvođač "Klimaoprema" ili slično, u RAL tonu prema zahtjevima arhitekture, sledećih dimenzija i količina: 225x225 mm | Delivery and installation of the aluminium overflow grid with one row of horizontal fixed, non-transparent slats with the counter-frame for installation on the door, type OASR, manufacturer "Klimaoprema" or similar, in RAL tone according to architectural requirements, following dimensions and quantities: 225x225 mm | kom/ pcs |  | 23 | 0
102. |  | Isporuka i montaža ventilacionog ventila od čeličnog lima, sa podesivim protokom vazduha, tip ZOV RAL 9010, proizvođača "Klimaoprema" ili sl, sledećih dimenzija i količina: | Delivery and installation of the ventilation valve made of sheet steel, with adjustable airflow, type ZOV RAL 9010, manufactured by "Klimaoprema" or similar, with the following dimensions and quantities:
|  | Ø100 mm | Ø100 mm | kom/ pcs |  | 22 | 0
|  | Ø125 mm | Ø125 mm | kom/ pcs |  | 4 | 0
|  | Ø150 mm | Ø150 mm | kom/ pcs |  | 16 | 0
103. |  | Isporuka i montaža okruglog mehaničkog regulatora konstantnog protoka za postavljanje u vazdušni kanal, tip KVR-R, proizvođača "Klimaoprema" ili sl, sledećih dimenzija i količina: Ø125 mm | Delivery and installation of the round mechanical regulator of constant flow for installation in the air channel, type KVR-R, manufactured by "Klimaoprema" or similar, with the following dimensions and quantities: Ø125 mm | kom/ pcs |  | 2 | 0
104. |  | Izrada, isporuka i montaža spiro kanala izrađenih od pocinkovanog čeličnog lima, za ubacivanje vazduha, uključujući fazonske komade (T-komade, redukcije, koljena, spojnice i sl), sledećih prečnika i količina (izolovani, izolacija uračunata u poziciji 14): | Making, delivery and installation of spiro channels made of galvanized steel sheet, for air injection, including shaped pieces (T-pieces, reductions, elbows, connectors, etc.) of the following diameters and quantities (insulated channels, insulation included in position 14):
|  | Ø100 mm | Ø100 mm | m1 |  | 77 | 0
|  | Ø125 mm | Ø125 mm | m1 |  | 7 | 0
|  | Ø160 mm | Ø160 mm | m1 |  | 100 | 0
|  | Ø200 mm | Ø200 mm | m1 |  | 45 | 0
|  | Ø250 mm | Ø250 mm | m1 |  | 16 | 0
105. |  | Za spojni i ovjesni i materijal, uzima se 20% od prethodne pozicije: | For connecting and hanging material, 20% of the previous position is taken: |  |  | 0.2 | 0
106. |  | Izrada, isporuka i montaža kanala i plenuma od pocinkovanog lima debljine 0,6-1,25 mm, prema DIN odnosno JUS normama. Kanale praviti sa duplim šavom, ukrućene dijagonalama (obračunava se prema razvijenoj površini lima, po srednjoj liniji kanala računajući fazonske komade): | Production, delivery and assembly of channels and plenums made of galvanized sheet with the thickness of 0.6-1.25 mm, according to DIN and JUS standards. Make the channels with the double seam, stiffened with diagonals (calculated according to the developed surface of the sheet, along the middle line of the channel, counting the shaped pieces): | kg |  | 1250 | 0
107. |  | Za izradu fazonskih komada, prirubnica od profilisanog gvožđa (MEZ profil i ugaonici), zaptivanje prirubnica sunđerastom samoljepljivom trakom, izradu vješaljki za nošenje vertikalnih kanala od "L" profila, izradu vješaljki za nošenje horizontalnih kanala od navojnih šipki Ø8 koje se čeličnim tiplovima vezuju za betonsku konstrukciju, izradu podmetača od ugaonih ("L") profila i sl. uzima se 50 % od prethodne pozicije: | For making shaped pieces, flanges from profiled iron (MEZ profile and corners), sealing flanges with spongy self-adhesive tape, making hangers for vertical channels from "L" profile, making hangers for horizontal channels from Ø8 threaded bars that are fixed to concrete construction by steel dowels, making pads from angular ("L") profiles, etc. 50% of the previous position is taken: |  |  | 0.5 | 0
108. |  | Isporuka i montaža termičke izolacije sa strukturnom parnom branom, samogasive, na bazi sintetičkog kaučuka, tip ACE proizvođača "Armacell" ili sl, uključujući lijepak i traku: Izolacija debljine 13 mm, samoljepljiva | Delivery and installation of thermal insulation with a structural vapour barrier, self-extinguishing, based on synthetic rubber, type ACE manufactured by "Armacell" or similar, including adhesive and tape: 13 mm thick insulation, self-adhesive | m2 |  | 222 | 0
109. |  | Isporuka i montaža izolovanog fleksi crijeva, prosječne dužine 1 m, komplet sa šelnama za stezanje crijeva, sledećih dimenzija i količina: Ø100 mm | Delivery and installation of insulated flexible hose, average length 1 m, set with hose clamps, following dimensions and quantities: Ø100 mm | m1 |  | 4 | 0
110. |  | Isporuka i montaža neizolovanog fleksi crijeva, prosječne dužine 1 m, komplet sa šelnama za stezanje crijeva, sledećih dimenzija i količina: | Delivery and installation of non-insulated flexible hose, average length 1 m, complete with hose clamps, the following dimensions and quantities:
|  | Ø100 | Ø100 | m1 |  | 30 | 0
|  | Ø125 | Ø125 | m1 |  | 10 | 0
|  | Ø150 | Ø150 | m1 |  | 25 | 0
IV. |  | VENTILACIJA ŠKOLE | VENTILATION OF SCHOOL |  |  | Ukupno/ Total | 0
V. |  | SPOLJAŠNJE JEDINICE I KLIMA KOMORA ZA GRIJANJE I KLIMATIZACIJU SALE | OUTDOOR UNITS AND AIR CONDITIONING CHAMBER FOR HEATING AND AIR CONDITIONING OF THE SPORTS HALL
111. |  | Isporuka i montaža vazduhom hlađenje spoljašnje jedinice VRF sistema za spoljašnju ugradnju Agregat se isporučuje u kompletu sa dvije spoljašnje jedinice i dva ahu kit-a proizvođač ,,PANASONIC" ili sl. Tip: U-16ME2E8+U-14ME2E8 + PAW-560MAH2(AHU kit (MAH) (Indoor Unit 1) System 1 ) + PAW-280MAH2 (AHU kit (MAH) (Indoor Unit 1) System 1) tip: U-16ME2E8+U-14ME2E8 rashladni fluid: R410A napajanje: 380-3Ph-50Hz broj rashladnih krugova: 1+1 dimenzije: 1842x1180x1000 x2 masa: 315+315 kg | Delivery and installation of the air-cooled outdoor unit of VRF system for outdoor installation: The unit is delivered with two outdoor units and two AHU kits manufactured by "PANASONIC" or similar. Type: U-16ME2E8+U-14ME2E8 + PAW-560MAH2(AHU kit (MAH) (Indoor Unit 1) System 1) + PAW-280MAH2 (AHU kit (MAH) (Indoor Unit 1) System 1) type: U-16ME2E8+U-14ME2E8; cooling fluid: R410A; power supply: 380-3Ph-50Hz; dimensions: 1842x1180x1000 x2; mass: 315+315 kg | komplet |  | 1 | 0
112. |  | Isporuka i montaža izolovanog bakarnog cjevovoda za povezivanje spoljašnjih jedinica i DX izmenjivača klima komore | Delivery and installation of the insulated copper pipeline for connecting outdoor units and DX air conditioner exchangers
|  | Ø 19,06 | Ø 19,06 | m1 |  | 20 | 0
|  | Ø 12.7 | Ø 12.7 | m1 |  | 20 | 0
113. |  | Isporuka i montaža račvi za medjusobno povezivanje spoljašnjih jedinica proizvođač ,,PANASONIC" | Delivery and installation of pieces for interconnecting outdoor units, manufacturer "PANASONIC."
|  | tip:CZ-P1350PH2BM | type:CZ-P1350PH2BM | kom/ pcs |  | 1 | 0
|  | tip:CZ-P680BK2BM | tyep:CZ-P680BK2BM | kom/ pcs |  | 1 | 0
114. |  | Isporuka i montaža klima komore za grijanje, klimatizaciju i ventilaciju fiskulturnu sale, tip Klimair2/Topair, proizvođača "OC IMP Klima " ili sl, sledećih karakteristika: *tip: Klimair2/Topair; *Spratna izvedba, unutrašnja ugradnja; *filtri tipa G4; *potis vazduha: protok 12000 m3/h, eksterni pad pritiska 300 Pa, temperatura 15,5 °C ljeti i 27°C zimi; *povrat vazduha: protok 12000 m3/h, eksterni pad pritiska 250 Pa; *količina svježeg vazduha: 4000 m3/h; *ventilatori sa frekventnim regulatorima | Delivery and installation of an air conditioning chamber for heating, air conditioning and ventilation of the Sports Hall, type Klimair2/Topair, manufactured by "OC IMP Klima" or similar, with the following characteristics: *type: Klimair2/Topair; *Storied design, internal installation; *type G4 filters; *air pressure: flow 12000 m3/h, external pressure drop 300 Pa, temperature 15.5 °C in summer and 27°C in winter; *air return: flow rate 12000 m3/h, external pressure drop 250 Pa; *amount of fresh air: 4000 m3/h; *fans with frequency regulators. | komplet/ set |  | 1 | 0
V. |  | SPOLJAŠNJE JEDINICE I KLIMA KOMORA ZA GRIJANJE I KLIMATIZACIJU SALE | OUTDOOR UNITS AND AIR CONDITIONING CHAMBER FOR HEATING AND AIR CONDITIONING OF THE SPORTS HALL |  |  | Ukupno/ Total | 0
VI. |  | VENTILACIJA I KANALSKI RAZVOD U FISKULTURNOJ SALI | VENTILATION AND CHANNEL- LINE IN THE SPORTS HALL
115. |  | Isporuka i montaža vrtložnog difuzora za ubacivanje vazduha, sa termostatskim regulatorom za optimizaciju ugla istrujavanja u odnosu na unutrašnju temperaturu, proizvođača "Klimaoprema" ili slično, obojen u RAL tonu prema zahtjevima arhitekture, sledećih dimenzija i količina: DVV 400-T | Delivery and installation of a vortex diffuser for air injection, with the thermostatic regulator for optimizing the angle of discharge in relation to the internal temperature, manufactured by "Klimaoprema" or similar, painted in RAL colour according to architectural requirements, following dimensions and quantities: DVV 400-T | kom/ pcs |  | 12 | 0
116. |  | Isporuka i montaža spoljne protivkišne žaluzine sa zaštitnom mrežicom, tip AFZV, proizvođač "Klimaoprema" ili slično, u RAL tonu prema zahtjevima arhitekture, sledećih dimenzija i količina: 1800x1400 | Delivery and installation of external rainproof blinds with protective mesh, type AFZV, manufacturer "Klimaoprema" or similar, in RAL tone according to architectural requirements, following dimensions and quantities: 1800x1400 | kom/ pcs |  | 2 | 0
117. |  | Isporuka i montaža aluminijske rešetke za dovod vazduha sa dva reda pojedinačno podesivih lamela u kompletu sa regulatorom protoka i ugradnim ramom, tip OAH2-L-UR, proizvođača "Klimaoprema" ili slično, u RAL tonu prema zahtjevima arhitekture, sledećih dimenzija i količina: 1000x500 | Delivery and installation of an aluminium grille for air supply with two rows of individually adjustable slats, complete with flow regulator and built-in frame, type OAH2-L-UR, manufactured by "Klimaoprema" or similar, in RAL colour according to architectural requirements, following dimensions and quantities: 1000x500 | kom/ pcs |  | 6 | 0
118. |  | Isporuka i montaža okruglog mehaničkog regulatora konstantnog protoka za ugradnju u spirokanalnoj mreži, tip RKP-C-N, proizvođača "Klimaoprema" ili sl, sledećih dimenzija i količina: Ø400 mm | Delivery and installation of the round mechanical regulator of constant flow for installation in a spiro channel pipeline, type RKP-C-N, manufactured by "Klimaoprema" or similar, with the following dimensions and quantities: Ø400 mm | kom/ pcs |  | 6 | 0
119. |  | Izrada, isporuka i montaža spiro kanala izrađenih od pocinkovanog čeličnog lima, za ubacivanje vazduha, uključujući fazonske komade (T-komade, redukcije, koljena, spojnice i sl), sledećih prečnika i količina (izolovani, izolacija uračunata u poziciji 15): | Production, delivery and assembly of spiro channels made of galvanized steel sheet, for air injection, including shaped pieces (T-pieces, reductions, elbows, connectors, etc.), of the following diameters and quantities (insulated channels, insulation included in position 15):
|  | Ø315 mm | Ø315 mm | m1 |  | 40 | 0
|  | Ø400 mm | Ø400 mm | m1 |  | 26 | 0
120. |  | Za spojni i ovjesni i materijal, uzima se 20% od prethodne pozicije: | For connecting and hanging material, 20% of the previous position is taken: |  |  | 0.2 | 0
121. |  | Izrada, isporuka i montaža kanala i plenuma od pocinkovanog lima debljine 0,6-1,25 mm, prema DIN odnosno JUS normama. Kanale praviti sa duplim šavom, ukrućene dijagonalama (obračunava se prema razvijenoj površini lima, po srednjoj liniji kanala računajući fazonske komade): | Production, delivery and assembly of channels and plenums made of galvanized sheet with the thickness of 0.6-1.25 mm, according to DIN and JUS standards. Make the channels with the double seam, stiffened with diagonals (calculated according to the developed surface of the sheet, along the middle line of the channel, counting the shaped pieces): | kg |  | 1850 | 0
122. |  | Za izradu fazonskih komada, prirubnica od profilisanog gvožđa (MEZ profil i ugaonici), zaptivanje prirubnica sunđerastom samoljepljivom trakom, izradu vješaljki za nošenje vertikalnih kanala od "L" profila, izradu vješaljki za nošenje horizontalnih kanala od navojnih šipki Ø8 koje se čeličnim tiplovima vezuju za betonsku konstrukciju, izradu podmetača od ugaonih ("L") profila i sl. uzima se 50 % od prethodne pozicije: | For making shaped pieces, flanges from profiled iron (MEZ profile and corners), sealing flanges with spongy self-adhesive tape, making hangers for vertical channels from "L" profile, making hangers for horizontal channels from Ø8 threaded bars that are fixed to concrete construction by steel dowels, making pads from angular ("L") profiles, etc. 50% of the previous position is taken: |  |  | 0.5 | 0
123. |  | Isporuka i montaža termičke izolacije sa strukturnom parnom branom, samogasive, na bazi sintetičkog kaučuka, tip ACE proizvođača "Armacell" ili sl, uključujući lijepak i traku: Izolacija debljine 19 mm, samoljepljiva | Delivery and installation of thermal insulation with a structural vapour barrier, self-extinguishing, based on synthetic rubber, type ACE manufactured by "Armacell" or similar, including adhesive and tape: | m2 |  | 190 | 0
VI. |  | VENTILACIJA I KANALSKI RAZVOD U FISKULTURNOJ SALI | VENTILATION AND CHANNEL- LINE IN THE SPORTS HALL |  |  | Ukupno/ Total | 0
VII. |  | GRAĐEVINSKI RADOVI VEZANI ZA POLAGANJE PREDIZOLOVANIH CIJEVI | CIVIL WORKS REFERS TO THE INSTALLATION OF PRE-INSULATED PIPES
124. |  | Mašinski iskop rova u zemlji III i IV kategorije: | Mechanical excavation in the soil of III and IV categories: | m3 |  | 217 | 0
125. |  | Ručno planiranje dna rova: | Manual trench subgrade planning: | m2 |  | 217 | 0
126. |  | Zatrpavanje rova pijeskom: | Filling the trench with sand: | m3 |  | 116 | 0
127. |  | Zatrpavanje rova materijalom iz iskopa: | Backfilling the trench with excavated material: | m3 |  | 101 | 0
128. |  | Odvoz viška zemlje na deponiju: | Transportl of excess soil to the landfill: | m3 |  | 116 | 0
129. |  | Obrada otvora oko cijevi na mjestima ulaza u objekat i izlaza kod toplkotnih pumpi, sa izradom hidroizolacije: | Treatment of the openings around the pipes at the points of entry into the building and exit of heat pumps, with the performing of waterproofing: | kom/ pcs |  | 12 | 0
VII. |  | GRAĐEVINSKI RADOVI VEZANI ZA POLAGANJE PREDIZOLOVANIH CIJEVI | CIVIL WORKS REFERS TO THE INSTALLATION OF PRE-INSULATED PIPES |  |  | Ukupno | 0
VIII. |  | OSTALI RADOVI | OTHER WORKS
130. |  | Pripremni radovi: a) obilazak gradilišta i uzimanje mjera na licu mjesta b) razmjeravanje i usaglašavanje sa ostalim izvođačima radova c) doprema materijala na objekat d) formiranje kancelarije i magacina, izrada skela, obilježavanje instalacije i uvođenje monterskih grupa u posao | Preparation works: a) visit the construction site and take measures on the location; b) comparison and coordination with other contractors; c) delivery of materials to the facility; d) establishment of office and warehouse, construction of scaffolding, marking of installation and introduction of fitter groups into the work; | komplet/ set |  | 1 | 0
131. |  | Unutrašnji transport opreme, materijala i alata | Internal transport of equipment, materials and tools | komplet/ set |  | 1 | 0
132. |  | Formiranje baze fotografija izvedenih radova na svim pozicijama, koje se predaju Investitoru nakon završetka posla na odgovarajućem memorijskom uređaju. Sve skrivene instalacije se fotografišu prije zatvaranja zidova i spuštenih plafona. | Creation of a database of photos of completed works in all positions, which are handed over to the Investor after completion of the work on the appropriate memory device. All hidden installations are photographed before walls, and suspended ceilings are closed. | komplet/ set |  | 1 | 0
133. |  | Završni radovi: a) proba na pritisak kompletne cijevne mreže b) višekratno ispiranje kompletne cijevne mreže (dok ne poteče potpuno čista voda) c) "topla" proba instalacije i puštanje u rad d) uregulisavanje i dokazivanje parametara instalacije (protoci u vodenom i vazdušnom dijelu instalacije) e) prikupljanje preostalog materijala i raščišćavanje gradilišta f) izrada uputstava za rukovanje i održavanje sa obukom korisnika. Uputstvo se predaje u tri primjerka, od kojih je jedan uramljen i postavljen na vidnom mjestu u podstanici. g) tehnički pregled, postupanje po primjedbama i kvalitativna predaja instalacije Korisniku nakon dobijanja upotrebne dozvole h) atesti isporučene opreme i garancija na opremu i instalaciju | Final works: a) pressure test of the complete pipelines; b) repeated flushing of the entire pipelines (until completely clean water flows out); c) "warm" trial installation and commissioning; d) regulating and proving installation parameters (flows in the water and air parts of the installation); e) collection of remaining material and cleaning of the construction site; g) technical audit, removing of objections and qualitative delivery of the installation to the User after obtaining the usage permit; h) certificates of delivered equipment and warranties on equipment and installation | komplet/ set |  | 1 | 0
134. |  | Izrada projekta izvedenog stanja, odštampano i ukoričeno u dva primjerka, kao i u elektronskom obliku na odgovarajućem disku. | Creation of the as-built design, printed and bound in two copies and in electronic form on the appropriate disc. | komplet/ set |  | 1 | 0
VIII. |  | OSTALI RADOVI | OTHER WORKS |  |  | Ukupno/ Total | 0
4.1. |  | REKAPITULACIJA TERMOTEHNIČKE INSTALACIJE | SUMMARY OF THERMOTECHNICAL INSTALLATION (HVAC)
I. |  | TOPLOTNA PUMPA I PODSTANICA ZA GRIJANJE I HLAĐENJE ŠKOLE | HEAT PUMP AND SUBSTATION FOR HEATING AND COOLING OF THE SCHOOL |  |  |  | 0
II. |  | INSTALACIJA VENTILATOR-KONVEKTORA | FAN-CONVECTOR INSTALLATION |  |  |  | 0
III. |  | SOLARNA INSTALACIJA | SOLAR INSTALLATION |  |  |  | 0
IV. |  | VENTILACIJA ŠKOLE | VENTILATION OF SCHOOL |  |  |  | 0
V. |  | SPOLJAŠNJE JEDINICE I KLIMA KOMORA ZA GRIJANJE I KLIMATIZACIJU SALE | OUTDOOR UNITS AND AIR CONDITIONING CHAMBER FOR HEATING AND AIR CONDITIONING OF THE SPORTS HALL |  |  |  | 0
VI. |  | VENTILACIJA I KANALSKI RAZVOD U FISKULTURNOJ SALI | VENTILATION AND CHANNEL- LINE IN THE SPORTS HALL |  |  |  | 0
VII. |  | GRAĐEVINSKI RADOVI VEZANI ZA POLAGANJE PREDIZOLOVANIH CIJEVI | CIVIL WORKS REFERS TO THE INSTALLATION OF PRE-INSULATED PIPES |  |  |  | 0
VIII. |  | OSTALI RADOVI | OTHER WORKS |  |  |  | 0
4.1. |  | UKUPNO TERMOTEHNIČKE INSTALACIJE | TOTAL THERMOTECHNICAL INSTALLATION (HVAC) |  |  |  | 0

## 4.2. SPRINKLER
Program obrazovanja Crne Gore / The education program of Montenegro
Predmjer - Izgradnja nove OŠ "Vladimir Nazor"/ Bill of Quantity - Construction of new Elementary School "Vladimir Nazor" MECHANICAL DESIGN OF STABLE FIRE EXTINGUISHING INSTALLATIONS - SPINKLER INSTALLATION
br/No | predmet/ subject | NASLOV | NAME | mjerna jedinica/ UNIT | pred.cijena/ unit price in € | Količina/ Quantity | Cijena u eurima (bez PDV-a)/ Amount in € (without VAT)
(a) | (b) | (c) |  | ( d ) | (e) | (f) | (g=e*f)
4.2. |  | MAŠINSKI PROJEKAT STABILNIH INSTALACIJA ZA GAŠENJE POŽARA | MECHANICAL DESIGN OF STABLE FIRE EXTINGUISHING INSTALLATIONS
|  | PREDMJER I PREDRAČUN SPRINKLER INSTALACIJA | BILL OF QUANTITY OF SPRINKLER INSTALLATION
I. |  | PUMPNO POSTROJENJE | THE PUMP STATION
1. |  | Pumpno postrojenje: Isporuka i ugradnja pumpnog postrojenja za transport i povišenje pritiska vode u sistemu za gašenje požara. Q = 970.81 l/min; H = 52.36 m. Sistem za povišenje pritiska kao potpuno automatski kompaktni sistem u svrhe gašenja požara u skladu sa DIN 12845. Sastoji se od 2 pumpe (glavna/rezervna) sa horizontalnim okvirom fundamenta – EN 733 – sa spojnicom za demontažu, elektromotorom i višestepenom vertikalnom električnom džokej pumpom, membranskom posudom (zapremina: 20 l), kao i sa komandnim ormarom po pumpi, koji je pričvršćen na čvrstoj nosećoj konstrukciji. | Pump station: Delivery and installation of the pump station for transport and increasing water pressure in the fire extinguishing system. Q = 970.81 l/min; H = 52.36 m. Pressure booster system as a fully automatic compact system for fire extinguishing purposes in accordance with DIN 12845. It consists of 2 pumps (main/reserve) with a horizontal foundation frame - EN 733 - with the coupling for disassembly, the electrical engine and the multi-stage vertical electrical jockey pump, with the membrane vessel (volume: 20 l), as well as with the control cabinet per pump, which is attached to the solid supporting structure. | komplet/set |  | 1 | 0
|  | Dva modela za elektromotor, oba opremljena kontrolerom, plus model za džokej pumpu, čvrsta konstrukcija od specijalnih profilnih delova sa prorezima za viljuškar i kuke, tako da se može obezbediti siguran transport. Držač podesiv po visini za izlazni razdelnik i specijalni okvir fundamenta značajno smanjuju prenos vibracija i povećavaju pouzdanost i radni vijek. Cirkulacija sa dvostrukim presostatom, manometrom, nepovratnim ventilom, ventilom (osiguranim od neovlašćenog uključivanja) za glavnu i rezervnu pumpu za automatsko startovanje. Kablovi su sakriveni u konstrukciji i zaštićeni su od vibracija i rezova. Serijski opremljen sa membranom koja je montirana direktno na kućištu glavne/rezervne pumpe, radi sprečavanja pregrejavanja pri nultom protoku. | Two models for electric motors, both equipped with a controller, plus the model for jockey pump, solid construction of special profile parts with slots for forklift and hooks, so that safe transportation can be ensured. Height-adjustable holder for the outlet manifold and special the foundation frame significantly reduces the transmission of vibrations and increases reliability and service life. Circulation with double pressure switch, manometer, non-return valve, and valve (secured from unauthorized switching on) for the main and reserve pump for automatic starting. There are cables hidden in the construction and protected from vibrations and cuts. Serially equipped with a membrane that is mounted directly on the main/reserve pump, to prevent overheating at zero flow
|  | Dva upravljačka uređaja za sisteme za gašenje požara u skladu sa EN 12845. Upravljački uređaji su ugrađeni u kućište od čeličnog lima, klasa zaštite IP54. Tip pumpnog postrojenja: EEJ (elektro radna+elektro rezervna+jockey pumpa) Radna tačka : Q= 970.81 l/min, H=52.36m. Snaga pumpe : P=(15kW+15kW+1.1kW) Mrežni priključak elektro pumpi : 3/400V/50Hz Nominalna struja jockey pumpe: 2.7A | Two control devices for fire extinguishing systems in accordance with EN 12845. The control devices are installed in a steel sheet box, protection class IP54. Type of pump station: EEJ (electrical working+electrical reserve+jockey pump) Flow-Head characteristic: Q= 970.81 l/min, H=52.36m. Pump power : P=(15kW+15kW+1.1kW) Electric pump mains connection : 3/400V/50Hz Nominal amperage of the jockey pump: 2.7A
2. |  | Prirubnički spoj sa ekscentričnim konusom DN 65x100 Ekscentrični konus sa standardnom prirubnicom, opremljen vakumetrom sa ventilom na gornjoj strani konusa. Ekscentrični konus služi za povećanje prečnika usisne cijevi i minimiziranje gubitka pritiska, kao i za držanje prigušne zaustavne klapne. | Flange connection with eccentric cone DN 65x100 Eccentric cone with standard flange, equipped with a vacuum gauge with a valve on the upper side of the cone. The eccentric cone serves to increase the diameter of the intake pipe and minimize pressure loss, as well as to hold the stifle stop flap. | kom/ pcs |  | 2 | 0
3. |  | Zaustavna klapna DN 100, PN 10. Prigušna zaustavna klapna služi za testiranje i održavanje, kao i za zamjenu pumpi u slučaju popravke. | Shut-off flap DN 100, PN 10. The damping shut-off flap is used for testing and maintenance, as well as for replacing pumps in the event repairs. | kom/ pcs |  | 2 | 0
4. |  | Mjerač protoka DN 65 Mjerač protoka služi za provjeru protoka | Flow meter DN 65 The flow meter to check the flow | kom/ pcs |  | 1 | 0
I. |  | PUMPNO POSTROJENJE | THE PUMP STATION |  |  | Ukupno | 0
II. |  | SPRINKLER INSTALACIJE | SPRINKLER INSTALLATION
5. |  | Kontrolni (alarmni) ventil - mokri DN100 Model sa ovalnim zasunom DN100, presostatom za nadzor stanja klapne, komorom za odloženo dejstvo presostata 2 manometra, ventilom za drenažu i ventilom za testiranje alarmnog zvona i bajpasom za izjednačavanje pritiska uzvodno i nizvodno od klapne sprinkler ventila. Sertifikat: FM | Control (alarm) valve - wet DN100 The model with DN100 oval gate valve, pressure switch for flap condition monitoring, the chamber for delayed action of pressure switch of 2 pressure gauges, drain valve and alarm bell test valve and bypass for pressure equalization upstream and downstream of the flap of sprinkler valve. Certifikate: FM | komp / set |  | 1 | 0
6. |  | Alarmno Zvono ulaz 3/4", izlaz 1" komplet fitinga sa odvajačem nečistoća 3/4" Sertifikat: FM | Alarm Bell inlet 3/4", outlet 1" fitting set with Impurity separator 3/4" Certificate: FM | komp / set |  | 1 | 0
7. |  | Mlaznice viseće, standardni odziv 3 mm staklena ampula 68°C, K=80, 1/2" NPT spoljni navoj, bijela Sertifikat: VdS | Hanging nozzles, the standard response, 3 mm glass ampoule, 68°C, K=80, , 1/2" NPT male thread, white. Certificate: VdS | kom/ pcs |  | 560 | 0
8. |  | Rozetne podesive za viseće mlaznice 1/2" NPT Ø73mm, bijele boje | Adjustable rosettes for hanging nozzles, 1/2" NPT Ø73mm, white color | kom/ pcs |  | 560 | 0
9. |  | Mlaznice viseće sa fleksi vezom, standardni odziv (rezervne) 3 mm staklena ampula 68°C, K=80, 1/2" NPT spoljni navoj, bijela Sertifikat: VdS | Hanging nozzles with flexi connection, standard response (spare), 3 mm glass ampoule, 68°C, K=80, 1/2" NPT male thread, white. Certificate: VdS | kom/ pcs |  | 24 | 0
10. |  | Ključ za montažu mlaznica Model W7 | Key wrench for installing nozzles Type W7 | kom/ pcs |  | 4 | 0
11. |  | Orman za rezervne mlaznice - viseće sa fleksi vezom Kapacitet 12 sprinkler mlaznice | Box for spare nozzles - hanging with flexi connection Capacity 12 sprinkler nozzles | kom/ pcs |  | 2 | 0
12. |  | Ovalni zasun Model PN10/16, DN100 Sertifikat: VdS | Oval valve Type PN10/16, DN100 Certificate: VdS | kom/ pcs |  | 9 | 0
13. |  | Odvajač nečistoća sa manometrima Model DN100 Sertifikat: VdS | Impurity separator with manometers Type DN100 Certificate: VdS | kom/ pcs |  | 1 | 0
14. |  | Manometar sa man. slavinom 1/2", 0-16 bar | Manometer with manual tap 1/2", 0-16 bar | kom/ pcs |  | 2 | 0
15. |  | Nepovratni ventil Model PN10/16, DN100 Sertifikat: VdS | Irreversible valv Type PN10/16, DN100 Certificate: VdS | kom/ pcs |  | 2 | 0
16. |  | Mikroprekidač daje informaciju o položaju zasuna (otvoren/djelimično otvoren) | Microswitch for giving information about the position of the valve (open/partially open) | kom/ pcs |  | 9 | 0
17. |  | Nosač za mikroprekidač DN50-DN300 | Microswitch holder DN50-DN300 | kom/ pcs |  | 9 | 0
18. |  | Gumeni kompenzator DN100 | Rubber compensator DN100 | kom/ pcs |  | 2 | 0
19. |  | Indikator protoka DN100 sa setom za testiranje Sertifikat: VdS | Flow indicator DN100 with test set Certificate: VdS | kom/ pcs |  | 3 | 0
20. |  | Ventil DN 50 sa faktorom k za testiranje k=80 | Valve DN 50 with factor k=80 for testing | kom/ pcs |  | 12 | 0
21. |  | Loptasti ventil Model DN50 (2”) Kv=211 | Ball valve Type DN50 (2”) Kv=211 | kom/ pcs |  | 12 | 0
22. |  | Priključak za vatrogasno vozilo ulaz 1xDN100 NPT, izlaz 2xDN65 NST sa klapnom unutar priključka | Fire-fighting engine connection inlet 1xDN100 NPT, outlet 2xDN65 NST with flep inside the connection | kom/ pcs |  | 1 | 0
23. |  | Brza spojnica (Štorc) DN75 NST | Quick coupling (Storz) DN75 NST | kom/ pcs |  | 2 | 0
24. |  | Brza slijepa spojnica sa lancem (Štorc) DN75 | Quick blind coupling with chain (Storz) DN75 | kom/ pcs |  | 2 | 0
25. |  | Slijepa prirubnica PN10/16, DN80 | Blind flange PN10/16, DN80 | kom/ pcs |  | 1 | 0
26. |  | Drenažni set Pocinkovane cijevi DN65, DN50, 40, DN32, DN25, pocinkovani fitinzi, lijevak kod sprinkler ventila, lijevak kod alarmnog zvona Sprovedeno do najbližeg slivnika | Drainage set Galvanized pipes DN65, DN50, 40, DN32, DN25, galvanized fittings, tube at the sprinkler valve, tube at the alarm bell. Drainaged to the nearest drain | kom/ pcs |  | 1 | 0
27. |  | Usisna korpa sa nepovratnom klapnom i protiv-vrtložnom pločom DN100 | Suction basket with non-return flap and anti-vortex plate DN100 | kom/ pcs |  | 1 | 0
28. |  | Nivostat | Water level control | kom/ pcs |  | 1 | 0
29. |  | Plovna kruška | Floating pear | kom/ pcs |  | 2 | 0
30. |  | Ventil sa plovkom za punjenje bazena protivpožarne vode DN50, visina ugradnje min. 200 mm | Float valve for filling the firefighting water tank DN50, installation height min. 200 mm | kom/ pcs |  | 2 | 0
31. |  | Čelične bešavne crne cijevi JUS C.B5.226 | Steel seamless black pipes JUS C.B5.226
|  | DN25(33,7x3,25) mm | DN25(33,7x3,25) mm | m1
|  |  |  | kg |  | 1.25 | 0
|  | DN32( 42,4 x 3,25) mm | DN32( 42,4 x 3,25) mm | m1
|  |  |  | kg |  | 1.25 | 0
|  | DN40(48.3 x 3,25) mm | DN40(48.3 x 3,25) mm | m1
|  |  |  | kg |  | 1.3 | 0
|  | DN50(60.3x3,65) mm | DN50(60.3x3,65) mm | m1
|  |  |  | kg |  | 1.3 | 0
|  | DN65(76.1x2,9) mm | DN65(76.1x2,9) mm | m1
|  |  |  | kg |  | 1.3 | 0
|  | DN80(88.9 x 3,2) mm | DN80(88.9 x 3,2) mm | m1
|  |  |  | kg |  | 1.3 | 0
|  | DN100 (114,3 x 3,6) mm | DN100 (114,3 x 3,6) mm | m1
|  |  |  | kg |  | 1.47 | 0
32. |  | FITING (crni) JUS M.B6.821 | FITTING (black) JUS M.B6.821
33. |  | T komad | T piece
|  | T komad DN 25 | T piece DN 25 | kom/ pcs |  | 148 | 0
|  | T komad DN 100 | T piece DN 100 | kom/ pcs |  | 12 | 0
|  | Koljeno 90° DN100 | Arc 90° DN100 | kom/ pcs |  | 7 | 0
|  | Koljeno 90° DN80 | Arc 90° DN80 | kom/ pcs |  | 4 | 0
34. |  | FITING (pocinkovani) Koljeno 90° DN25 | FITTING (galvanized) Arc 90° DN25 | kom/ pcs |  | 73 | 0
35. |  | Redukcije | Reductions | kom/ pcs
|  | Redukcija DN80-DN65 | Reduction DN80-DN65 | kom/ pcs |  | 4 | 0
|  | Redukcija DN65-DN50 | Reduction DN65-DN50 | kom/ pcs |  | 4 | 0
|  | Redukcija DN50-DN40 | Reduction DN50-DN40 | kom/ pcs |  | 31 | 0
|  | Redukcija DN40-DN32 | Reduction DN40-DN32 | kom/ pcs |  | 63 | 0
|  | Redukcija DN32-DN25 | Reduction DN32-DN25 | kom/ pcs |  | 92 | 0
36. |  | Mufne (nazuvice) | Muffs (niples)
|  | Muf (nazuvica) DN25 | Muff (nipple) DN25 | kom/ pcs |  | 560 | 0
|  | Redukovani muf DN25 - DN20 | Reduced muff DN25 - DN20 | kom/ pcs |  | 560 | 0
37. |  | Fleksibilno crijevo (Vds) 20 L=500 mm | Flexible hose (Vds) 20 L=500 mm | kom/ pcs |  | 560 | 0
38. |  | Oslonci sprinklerskih grana | Sprinkler pipeline supports
|  | tip O2 za DN100 | type O2 for DN100 | kom/ pcs |  | 113 | 0
|  | tip O1 za DN25 | type O1 for DN25 | kom/ pcs |  | 392 | 0
|  | tip O1 za DN32 | type O1 for DN32 | kom/ pcs |  | 60 | 0
|  | tip O1 za DN40 | type O1 for DN40 | kom/ pcs |  | 41 | 0
|  | tip O1 za DN50 | type O1 for DN50 | kom/ pcs |  | 55 | 0
|  | tip O1 za DN65 | type O1 for DN65 | kom/ pcs |  | 17 | 0
|  | tip O1 za DN80 | type O1 for DN80 | kom/ pcs |  | 21 | 0
II. |  | SPRINKLER INSTALACIJE | SPRINKELR INSTALLATIONS |  |  | Ukupno/ Total | 0
III. |  | PRIPREMNO ZAVRŠNI RADOVI | PREPARATORY-FINAL WORKS
39. |  | Montaža, bušenje rupa kroz zidove i grede, farbanje cijevi, potrošni materijal | Installation, drilling holes through walls and beams, painting pipes, auxiliary material | pauš/ LS |  | 1 | 0
40. |  | Snimanje i izrada projekta izvedenog stanja u tri primjerka | Survey and preparation of as-built design in three copies | pauš/ LS |  | 1 | 0
41. |  | Ispitivanje i puštanje u rad | Testing and commissioning | pauš/ LS |  | 1 | 0
42. |  | Obuka i izrada uputstava za rad | Training of users and preparation of user manual | pauš/ LS |  | 1 | 0
43. |  | Transport (spoljni i unutar objekta) | Transport (external and internal) | pauš/ LS |  | 1 | 0
III. |  | PRIPREMNO ZAVRŠNI RADOVI | PREPARATORY-FINAL WORKS |  |  | Ukupno/ Total | 0
4.2. |  | REKAPITULACIJA - MAŠINSKI PROJEKAT STABILNIH INSTALACIJA ZA GAŠENJE POŽARA | SUMMARY MECHANICAL DESIGN OF STABLE FIRE EXTINGUISHING INSTALLATIONS
I. |  | PUMPNO POSTROJENJE | THE PUMP STATION |  |  |  | 0
II. |  | SPRINKLER INSTALACIJE | SPRINKLER INSTALLATION |  |  |  | 0
III. |  | PRIPREMNO ZAVRŠNI RADOVI | PREPARATORY-FINAL WORKS |  |  |  | 0
4.2. |  | UKUPNO - MAŠINSKI PROJEKAT STABILNIH INSTALACIJA ZA GAŠENJE POŽARA | SUMMARY MECHANICAL DESIGN OF STABLE FIRE EXTINGUISHING INSTALLATIONS |  |  |  | 0

## 5. Zašt od pož-FIRE PR
Program obrazovanja Crne Gore / The education program of Montenegro
Predmjer - Izgradnja nove OŠ "Vladimir Nazor"/ Bill of Quantity - Construction of new Elementary School "Vladimir Nazor" ZAŠTITA OD POŽARA / FIRE PROTECTION
br/No | predmet/ subject | NASLOV | NAME | mjerna jedinica/ UNIT | pred.cijena/ unit price in € | Količina/ Quantity | Cijena u eurima (bez PDV-a)/ Amount in € (without VAT)
(a) | (b) | (c) |  | ( d ) | (e) | (f) | (g=e*f)
5 . |  | ZAŠTITA OD POŽARA | FIRE PROTECTION
|  | PREDMJER I PREDRAČUN ZAŠTITE OD POŽARA | BILL OF QUANTITY OF FIRE PROTECTION
I. |  | APARATI | DEVICES
1. |  | Ručni aparati za početno gašenje požara tip S-9A | Hand-held devices for initial fire extinguishing type S - 9A | kom/pcs |  | 33 | 0
2. |  | Ručni aparati za početno gašenje požara tip CO2-5kg | Hand-held devices for initial fire extinguishing type CO2 - 5 kg | kom/pcs |  | 9 | 0
3. |  | Ormar za aparate za početno gašenje požara tip S-9A, dimenzije 300x680x240 (ŠxVxD) | Cabinet for fire extinguishers type S - 9A, dimensions 300 x 680 x 240 mm (WxHxD) | kom/pcs |  | 19 | 0
4. |  | Ormar za aparate za početno gašenje požara tip CO2-5kg, dimenzije 290x840x250 (ŠxVxD) | Cabinet for fire extinguishers type CO2 - 5 kg, dimensions 290x840x250 mm (WxHxdD) | kom/pcs |  | 4 | 0
I. |  | APARATI | DEVICES |  |  | Ukupno | 0
5 . |  | REKAPITULACIJA - ZAŠTITA OD POŽARA | SUMMARY- FIRE PROTECTION
I. |  | APARATI | DEVICES |  |  |  | 0
5 . |  | UKUPNO - ZAŠTITA OD POŽARA | TOTAL-FIRE PROTECTION |  |  |  | 0

## 9.Pejzaž.arh-SCENERY
Program obrazovanja Crne Gore / The education program of Montenegro
Predmjer - Izgradnja nove OŠ "Vladimir Nazor"/ Bill of Quantity - Construction of new Elementary School "Vladimir Nazor" LANDSCAPE ARCHITECTURE - SCENERY
br/No | predmet/ subject | NASLOV | NAME | mjerna jedinica/ UNIT | predt.cijena/ unit price in € | Količina/ Quantity | Cijena u eurima (bez PDV-a)/ Amount in € (without VAT)
(a) | (b) | (c) |  | ( d ) | (e) | (f) | (g=e*f)
9 . |  | PEJZAŽNA ARHITEKTURA | LANDSCAPE ARCHITECTURE - SCENERY
|  | PREDMJER I PREDRAČUN PEJZAŽNE ARHITEKTURE | BILL OF QUANTITY OF LANDSCAPE ARCHITECTURE - SCENERY
I. |  | PRIPREMNI RADOVI | PREPARATORY WORKS
1. |  | Ukljanjanje postojećeg zelenila | Removal of existing greenery | kom/pcs |  | 13 | 0
2. |  | Primjena mjera njege na postojecem zelenilu koje ostaje na lokaciji | Application of care measures on the existing greenery that remains on the site | kom/pcs |  | 69 | 0
3. |  | Obilježavanje, kolčenje i planiranje slobodnih površina. | Marking, staking-out and planning of accessible areas. | pauš/LS |  | 1 | 0
I. |  | PRIPREMNI RADOVI | PREPARATORY WORKS |  |  | UkupnoTotal | 0
II. |  | ZEMLJANI RADOVI | EARTHWORKS
4. |  | Raščišćavanje terena i mašinsko skidanje gornjeg sloja zemlje od 5 cm sa odvozom na deponiju. | Land clearing and mechanical removal of the 5 cm layer of topsoil with transport to the landfill. | m3 |  | 323 | 0
5. |  | Freziranje i gruba nivelacija travne površine. | Milling and rough levelling of the grass surface | m2 |  | 6476 | 0
6. |  | Nabavka i nasipanje plodne baštenske zemlje sa iskopom, transportom i razastiranjem (umjesto skinutog neplodnog materijala). Grubo i fino planiranje 50% budućeg travnjaka I postojeće travne površine. Dubina sloja nasipanja 5 cm. | Procurement and filling of fertile garden soil with excavation, transport and spreading (instead of excavated infertile material). Rough and fine planning of 50% of the future grassland and the existing grass area. Depth of filling layer 5 cm. | m3 |  | 323 | 0
7. |  | Nabavka plodnog supstrata za sadnju u sadnim jamama na terenu. | Procurement of fertile substrate for planting in planting pits in the field. | m3 |  | 21 | 0
8. |  | Nabavka i isporuka tresetnog đubriva. | Procurement and delivery of peat fertilizer. | džak/bags |  | 20 | 0
II. |  | ZEMLJANI RADOVI | EARTHWORKS |  |  | UkupnoTotal | 0
III. |  | NABAVKA I SADNJA SADNOG MATERIJALA | PROCUREMENT AND PLANTING OF PLANTING MATERIAL
|  | Četinarsko drveće | Coniferous trees
9. |  | Pinus pinea Clt.90, H min 3,50 m, O. 18/20 cm, Standard | Pinus pinea Clt.90, H min 3,50 m, O. 18/20 cm, Standard | kom/pcs |  | 5 | 0
10. |  | Cupressus sempervirens „Stricta“ Clt.30, H 2.00/ 3,00 m | Cupressus sempervirens „Stricta“ Clt.30, H 2.00/ 3,00 m | kom/pcs |  | 6 | 0
|  | Lišćarsko drveće | Deciduous trees
11. |  | Osmanthus fragrans New line Clt 230 2.00/2.50 | Osmanthus fragrans New line Clt 230 2.00/2.50 | kom/pcs |  | 3 | 0
12. |  | Koelreuteria paniculate Clt 90, O 18/20 cm H 3,0/3,5 m | Koelreuteria paniculate Clt 90, O 18/20 cm H 3,0/3,5 m | kom/pcs |  | 6 | 0
13. |  | Lagerstroemia indica Caroline beauty Clt.55, O 10/12 h 2.00/2.50 | Lagerstroemia indica Caroline beauty Clt.55, O 10/12 h 2.00/2.50 | kom/pcs |  | 8 | 0
14. |  | Callistemon citrinus Clt.45, H 1,50/1,75 | Callistemon citrinus Clt.45, H 1,50/1,75 | kom/pcs |  | 6 | 0
|  | Modul živa ograda - MO | Module shrubs fence (hedges) - MO |  |  | 1 | 0
15. |  | Photinia x fraseri "Red Robin"- živa ograda Clt.18, H 1,50 m | Photinia x fraseri "Red Robin"- shrubs fence (hedges) Clt.18, H 1,50 m | kom/pcs |  | 60 | 0
16. |  | Cupressocyparis leylandii Clt.35, H 3,00 m Formiran u živu ogradu visine 3 m | Cupressocyparis leylandii Clt.35, H 3,00 m Formed into the 3 m high hedge | kom/pcs |  | 28 | 0
17. |  | Photinia x fraseri „Red Robin“ - h 3,0 m standard Clt. 90 14/16 | Photinia x fraseri „Red Robin“ - h 3,0 m standard Clt. 90 14/16 | kom/pcs |  | 4 | 0
|  | Modul 1 - M1 | Module 1 - M1 |  |  | 4 | 0
18. |  | Laurus nobilis Cone Clt.70 H 2.00 m 2,50/3,00 | Laurus nobilis Cone Clt.70 H 2.00 m 2,50/3,00 | kom/pcs |  | 12 | 0
19. |  | Pittosporum tobira “Nanum” Clt.10, H 0,60/0,80 m | Pittosporum tobira “Nanum” Clt.10, H 0,60/0,80 m | kom/pcs |  | 8 | 0
20. |  | Lavandula angustifolia 'Hidcote' Clt. 10 | Lavandula angustifolia 'Hidcote' Clt. 10 | kom/pcs |  | 32 | 0
21. |  | Liriope muscari Variegata 5 kom/m2 za pokrivač tla Clt.3 | Liriope muscari Variegata 5 kom/m2 for ground cover Clt.3 | kom/pcs |  | 480 | 0
22. |  | Plastični graničnici | Plastic limiters | m1 |  | 92 | 0
23. |  | Geotekstil sloj filterske zaštite VLF-200 (rolna 100x2 m) | Geotextile layer of filter protection VLF-200 (roll 100x2 m) | m2 |  | 92 | 0
|  | Modul 2 - M2 | Module 2 - M2 |  |  | 1
24. |  | Pittosporum tobira “Nanum” Clt.10, H 0,60/0,80 | Pittosporum tobira “Nanum” Clt.10, H 0,60/0,80 | kom/pcs |  | 3 | 0
25. |  | Lavandula angustifolia 'Hidcote' Clt. 10 | Lavandula angustifolia 'Hidcote' Clt. 10 | kom/pcs |  | 16 | 0
26. |  | Artemisia schmidtiana Silver maund Clt. 10 | Artemisia schmidtiana Silver maund Clt. 10 | kom/pcs |  | 40 | 0
27. |  | Liriope muscari Clt. 10 | Liriope muscari Clt. 10 | kom/pcs |  | 20 | 0
28. |  | Dekorativni kameni obluci, izrazito bijele boje, u sloju od 5 cm; granulacija 0,8-2 cm; oblik: nepravilan i okrugao (P=10,00 m2) | Decorative stone pebbles, distinctly white, in the layer of 5 cm; granulation 0.8-2 cm; shape: irregular and round (P=10.00 m2) | m3 |  | 0.5 | 0
29. |  | Plastični graničnici | Plastic limiters | m1 |  | 22 | 0
|  | Ostalo | Others
30. |  | Travnjak: Priprema terena, planiranje, nabavka i sjetva trave, sa valjanjem i zalivanjem (po opisu). Površina travnjaka sa smješom otpornom na uslove polusijenke, humusiranje 5cm | Grassland: Ground preparation, planning, procurement and sowing of grass, with rolling and watering (according to description). Lawn surface with mixture resistant to semi-shade conditions, hummus 5 cm | m2 |  | 6476 | 0
|  | Sadnja dendrološkog materijala | Planting dendrological material
31. |  | Sadnja drveća: sadnja zdravih rasadnički odnjegovanih sadnica visine prema specifikaciji. Na mjestima označenim u projektu iskopati jame kružnog presjeka i cilindričnog oblika i nasuti plodni supstrat. Iskop rupa prema veličini sadnice, najbolje da je sadna jama minimum 30% veća od busena sadnice. Izvršiti ankerisanje i učvršćivanje. | Planting trees: planting healthy seedlings raised in plant nurseries of specified height. In the places marked in the project, excavate pits with the circular cross-section and the cylindrical shape and pour fertile substrate. Excavation of holes according to the size of the seedling, it is best if the planting pit is at least 30% larger than the sod of the seedling. Finally, carry out anchoring and fixing. | kom/pcs |  | 38 | 0
32. |  | Žbunje i žive ograde: sadnja zdravih rasadnički odnjegovanih sadnica. Iskop rupa prema veličini sadnice, najbolje da je sadna jama minimum 30% veća od busena sadnice. | Shrubs and hedges:planting healthy seedlings raised in plant nurseries. Excavation of holes according to the size of the seedling, it is best if the planting pit is at least 30% larger than the sod of the seedling. | kom/pcs |  | 111 | 0
33. |  | Bordure, perene: sadnja zdravih rasadnički odnjegovanih sadnica. Iskop rupa prema veličini sadnice, najbolje da je sadna jama minimum 30% veća od busena sadnice. | Borders, feather beds: planting healthy seedlings raised in plant nurseries. Excavation of holes according to the size of the seedling, it is best if the planting pit is at least 30% larger than the sod of the seedling. | kom/pcs |  | 588 | 0
III. |  | NABAVKA I SADNJA SADNOG MATERIJALA | PROCUREMENT AND PLANTING OF PLANTING MATERIAL |  |  | UkupnoTotal | 0
IV. |  | OSTALI RADOVI | OTHER WORKS
34. |  | Ankerisanje, orezivanje i učvršćivanje grupacija stabala leylandija u zivoj ogradi prema tehničkom opisu | Anchoring, pruning and strengthening of groups of leylandii trees in the hedge according to the technical description | kom/pcs |  | 28 | 0
35. |  | Ankerisanje i učvršćivanje svih stabala kao i podzemno ankerisanje stabala Pinus pinea i u projektu. | Anchoring and strengthening of all trees and underground anchoring of Pinus pine trees in the design. | kom/pcs |  | 5 | 0
IV. |  | OSTALI RADOVI | OTHER WORKS |  |  | UkupnoTotal | 0
V. |  | NAVODNJAVANE | WATERING
36. |  | Projektovanje, nabavka i ugradnja sistema za zalivanje (prskalice i kap po kap) | Design, procurement and installation of watering systems (sprinklers and drippers) | m2 |  | 6476 | 0
V. |  | NAVODNJAVANE | WATERING |  |  | UkupnoTotal | 0
VI. |  | ODRŽAVANJE | MAINTENANCE
37. |  | Održavanje zelenila uz primjenu svih potrebnih mjera (orezivanje, njega travnjaka, zalivanje i sl.). Tokom formiranja zelenila u periodu od 1 godine nakon sadnje održavanje iznosi 20% od ukupne sume pozicija Sadnja i nabavka dendroloskog materijala. | Maintenance of greenery with all necessary measures (pruning, lawn care, watering, etc.). During the formation of vegetation in 1 year after planting, maintenance amounts to 20% of the total sum of positions planting and procurement of dendrological material. | m2 | 20% | 0 | 0
VI. |  | ODRŽAVANJE | MAINTENANCE |  |  | UkupnoTotal | 0
9 . |  | REKAPITULACIJA - PEJZAŽNA ARHITEKTURA | SUMMARY OF LANDSCAPE ARCHITECTURE - SCENERY
I. |  | PRIPREMNI RADOVI | PREPARATORY WORKS |  |  |  | 0
II. |  | ZEMLJANI RADOVI | EARTHWORKS |  |  |  | 0
III. |  | NABAVKA I SADNJA SADNOG MATERIJALA | PROCUREMENT AND PLANTING OF PLANTING MATERIAL |  |  |  | 0
IV. |  | OSTALI RADOVI | OTHER WORKS |  |  |  | 0
V. |  | NAVODNJAVANE | WATERING |  |  |  | 0
VI. |  | ODRŽAVANJE | MAINTENANCE |  |  |  | 0
9. |  | UKUPNO - PEJZAŽNA ARHITEKTURA | TOTAL LANDSCAPE ARCHITECTURE - SCENERY |  |  |  | 0

## 10. Signalizacija-TR.SIGN
Program obrazovanja Crne Gore / The education program of Montenegro
Predmjer - Izgradnja nove OŠ "Vladimir Nazor"/ Bill of Quantity - Construction of new Elementary School "Vladimir Nazor" SAOBRAĆAJNA SIGNALIZACIJA/ TRAFFIC SIGNALIZATION
br/No | predmet/ subject | NASLOV | NAME | mjerna jedinica/ UNIT | predt.cijena/ unit price in € | Količina/ Quantity | Cijena u eurima (bez PDV-a)/ Amount in € (without VAT)
(a) | (b) | (c) |  | ( d ) | (e) | (f) | (g=e*f)
10 . |  | SAOBRAĆAJNA SIGNALIZACIJA | TRAFFIC SIGNALIZATION
|  | PREDMJER I PREDRAČUN SAOBRAĆAJNE SIGNALIZACIJE | BILL OF QUANTITY OF TRAFFIC SIGNALIZATION
I. |  | VERTIKALNA SIGNALIZACIJA | VERTICAL SIGNS
1. |  | Standardni saobraćajni znak -II -2 (obavezno zaustavljanje) osmougaonik krug ø 600 mm Reflektujućih osobina, klase II, isporuka i doprema do mjesta postavljanja sa svim elementima za pričvršćivanje za nosač (pojačanje,obujmice, zavrtnji, manžetne i dr.), kao i montaža znaka na ugrađeni nosač. | Standard traffic sign -II -2 (mandatory stop) octagon circle ø 600 mm Reflective properties, class II, supply and delivery to the place of installation with all elements for fixing to the support (reinforcement, clamps, screws, cuffs, etc.), and installation of the sign on the installed support | kom/pcs |  | 2 | 0
2. |  | Standardni saobraćajni znak -II -30.2 max dozvoljena brzina) krug ø 600 mm Reflektujućih osobina, klase II, isporuka i doprema do mjesta postavljanja sa svim elementima za pričvršćivanje za nosač (pojačanje,obujmice, zavrtnji, manžetne i dr.), kao i montaža znaka na ugrađeni nosač. | Standard traffic sign -II -30.2 (max permitted speed) circle ø 600 mm Reflective properties, class II, supply and delivery to the place of installation with all elements for fixing to the support (reinforcement, clamps, screws, cuffs, etc.), and installation of the sign on the installed support | kom/pcs |  | 2 | 0
3. |  | Standardni saobraćajni znak - III-6 (Pješački prelaz) kvadrat 600x600mm Reflektujućih osobina, klase II, isporuka i doprema do mjesta postavljanja sa svim elementima za pričvršćivanje za nosač (pojačanje,obujmice, zavrtnji, manžetne i dr.), kao i montaža znaka na ugrađeni nosač. | Standard traffic sign - III-6 (Pedestrian crossing) square 600x600mm Reflective properties, class II, supply and delivery to the place of installation with all elements for fixing to the support (reinforcement, clamps, screws, cuffs, etc.), and installation of the sign on the installed support | kom/pcs |  | 1 | 0
4. |  | Standardni saobraćajni znak - III-35 (parking) krug R-600mm Reflektujućih osobina, klase II, isporuka i doprema do mjesta postavljanja sa svim elementima za pričvršćivanje za nosač (pojačanje,obujmice, zavrtnji, manžetne i dr.), kao i montaža znaka na ugrađeni nosač. | Standard traffic sign - III-35 (parking lot) circle ø 600 mm Reflective properties, class II, supply and delivery to the place of installation with all elements for fixing to the support (reinforcement, clamps, screws, cuffs, etc.), and installation of the sign on the installed support | kom/pcs |  | 8 | 0
5. |  | Dopunska tabla -IV-14 (OSI) krug R-600mm Reflektujućih osobina, klase II, isporuka i doprema do mjesta postavljanja sa svim elementima za pričvršćivanje za nosač (pojačanje,obujmice, zavrtnji, manžetne i dr.), kao i montaža znaka na ugrađeni nosač. | Additional board -IV-14 (PWD) circle ø 600 mm Reflective properties, class II, supply and delivery to the place of installation with all elements for fixing to the support (reinforcement, clamps, screws, cuffs, etc.), and installation of the sign on the installed support | kom/pcs |  | 6 | 0
6. |  | Stub nosač saobraćajnog znaka - jednostubni cijevni nosač dužine 4,00 m Od čelične pocinčane cijevi jednoličnog presjeka i debljine prečnika 2'' , isporuka i doprema do mjesta postavljanja sa izradom betonskog temelja i ugradnjom stuba nosača u betonski temelj. | Traffic sign support pole - single-column pipe support with the length of 4,00 m Made of galvanized steel pipe with a uniform cross-section and a diameter of 2", supply and delivery to the place of installation with the performing of a concrete foundation and the installation of the support pole in the concrete foundation | kom/pcs |  | 3 | 0
7. |  | Stub nosač saobraćajnog znaka - jednostubni cijevni nosač dužine 3,70 m Od čelične pocinčane cijevi jednoličnog presjeka i debljine prečnika 2'' , isporuka i doprema do mjesta postavljanja sa izradom betonskog temelja i ugradnjom stuba nosača u betonski temelj. | Traffic sign support pole - single-column pipe support with the length of 3,70 m Made of galvanized steel pipe with a uniform cross-section and a diameter of 2", supply and delivery to the place of installation with the performing of a concrete foundation and the installation of the support pole in the concrete foundation | kom/pcs |  | 6 | 0
8. |  | Stub nosač saobraćajnog znaka - jednostubni cijevni nosač dužine 3,40 m Od čelične pocinčane cijevi jednoličnog presjeka i debljine prečnika 2'' , isporuka i doprema do mjesta postavljanja sa izradom betonskog temelja i ugradnjom stuba nosača u betonski temelj. | Traffic sign support pole - single-column pipe support with the length of 3,40 m Made of galvanized steel pipe with a uniform cross-section and a diameter of 2", supply and delivery to the place of installation with the performing of a concrete foundation and the installation of the support pole in the concrete foundation | kom/pcs |  | 1 | 0
I. |  | VERTIKALNA SIGNALIZACIJA | VERTICAL SIGNS |  |  | Ukupno/Total | 0
II. |  | HORIZONTALNA SIGNALIZACIJA | HORIZONTAL SIGNALIZATION
9. |  | Poprečna linija: -Pješački prelazi dužine 2m Obilježavanje kolovoza bijelom bojom reflektujućih osobina sa prethodnim čišćenjem i odmašćavanjem kolovoza, razmjeravanje bojanih površina i farbanje kolovoza bijelom bojom(prema standardu EN 1436). | Transverse line: -Pedestrian crossings 2m long Marking the pavement with white reflective paint with previously cleaning and degreasing of the pavement, measuring the painted surfaces and painting the pavement with white paint (according to standard EN 1436) | m2 |  | 7.5 | 0
10. |  | Poprečna linija: -Zaustavna linija širine 0.5mm Obilježavanje kolovoza bijelom bojom reflektujućih osobina sa prethodnim čišćenjem i odmašćavanjem kolovoza, razmjeravanje bojanih površina i farbanje kolovoza bijelom bojom (prema standardu EN 1436). | Transverse line: - Stop line, width 0.5mm Marking the pavement with white reflective paint with previously cleaning and degreasing of the pavement, measuring the painted surfaces and painting the pavement with white paint (according to standard EN 1436) | m2 |  | 5.5 | 0
11. |  | Uzdužne linije b=0.10 m : -Puna linija Obilježavanje kolovoza bijelom bojom reflektujućih osobina sa prethodnim čišćenjem i odmašćavanjem kolovoza, razmjeravanje bojanih površina i farbanje kolovoza bijelom bojom(prema standardu EN 1436). | Longitudinal lines b=0.10 m: - solid line Marking the pavement with white reflective paint with previously cleaning and degreasing of the pavement, measuring the painted surfaces and painting the pavement with white paint (according to standard EN 1436) | m |  | 427 | 0
12. |  | Uzdužne linije b=0.12 m : -Isprekidana linija 3+3 Obilježavanje kolovoza bijelom bojom reflektujućih osobina sa prethodnim čišćenjem i odmašćavanjem kolovoza, razmjeravanje bojanih površina i farbanje kolovoza bijelom bojom(prema standardu EN 1436). | Longitudinal lines b=0.12 m: - interrupted line 3+3 Marking the pavement with white reflective paint with previously cleaning and degreasing of the pavement, measuring the painted surfaces and painting the pavement with white paint (according to standard EN 1436) | m |  | 67 | 0
II. |  | HORIZONTALNA SIGNALIZACIJA | HORIZONTAL SIGNALIZATION |  |  | Ukupno/Total | 0
10 . |  | REKAPITULACIJA - SAOBRAĆAJNA SIGNALIZACIJA | SUMMARY - TRAFFIC SIGNALIZATION
I. |  | VERTIKALNA SIGNALIZACIJA | VERTICAL SIGNS |  |  |  | 0
II. |  | HORIZONTALNA SIGNALIZACIJA | HORIZONTAL SIGNALIZATION |  |  |  | 0
10 . |  | UKUPNO - SAOBRAĆAJNA SIGNALIZACIJA | TOTAL - TRAFFIC SIGNALIZATION |  |  |  | 0

## 11. Pr opremanja-FURNITURE
Program obrazovanja Crne Gore / The education program of Montenegro
Predmjer - Izgradnja nove OŠ "Vladimir Nazor"/ Bill of Quantity - Construction of new Elementary School "Vladimir Nazor" PROJEKAT OPREMANJE ŠKOLA I SALE/ DESIGN OF FURNITURE AND EQUIPMENT FOR THE SCHOOL AND SPORTS HALL
br/No | predmet/ subject | NASLOV | NAME | mjerna jedinica/ UNIT | predt.cijena/ unit price in € | Količina/ Quantity | Cijena u eurima (bez PDV-a)/ Amount in € (without VAT)
(a) | (b) | (c) |  | ( d ) | (e) | (f) | (g=e*f)
11 . |  | PROJEKAT OPREMANJA ŠKOLE I SALE | DESIGN OF FURNITURE AND EQUIPMENT FOR SCHOOL AND HALL
|  | PREDMJER I PREDRAČUN OPREMANJA ŠKOLE I SALE | BILL OF QUANTITY OF FURNITURE AND EQUIPMENT FOR SCHOOL AND HALL
I. |  | SERIJSKA OPREMA | SERIAL EQUIPMENT
1. |  | GO1- GARDEROBNI ORMAN - 60x50x180cm ● Nabavka i isporuka garderobnih metalnih kasetnih ormana. Izrađeni su od čeličnog lima visokog kvaliteta odgovarajuće debljine, jake varene konstrukcije, sa 4 kabine. Vrata ormana opremljena su standardnom cilindar bravom sa ključem, a posjeduju ventilacione otvore u gornjoj i donjoj zoni. Unutar svake kabine ormana nalazi se polica za odlaganje stvari, šipka za kačenje, kuke za kačenje odjeće. ● Dozvoljeno je odstupanje +- 5% ● Boja vrata na kabinama - RAL 1023, a ostatak plakara u boji - RAL 7035. | GO1-WARDROBE - 60x50x180cm ● Procurement and delivery of wardrobe metal cassettes. They are made of high-quality sheet steel of appropriate thickness and reinforced construction, with four cabins. The cabinet doors have a standard cylindrical lock and ventilation openings in the upper and lower zones. Inside each wardrobe cabinet are shelves for storing things, hanging rods and hooks for hanging clothes. A deviation of +/- 5% is allowed ● Door colour on cabins - RAL 1023, rest of closets in colour - RAL 7035. | kom/pcs |  | 128 | 0
2. |  | AO1 - ARHIVSKI ORMAN - 92x42x195cm ● Nabavka i isporuka metalnih arhivskih ormana. Izrađeni su od kvalitetnog čeličnog lima odgovarajuće debljine. Ormani posjeduju dvokrilna vrata sa velikim uglom otvaranja, a unutar istih nalaze se police koje imaju mogućnost pomjeranja. Nosivost police je 50kg. Vrata ormana su opremljena kvalitetnom cilindar bravom sa trosmjernim mehanizmom zatvaranja. ● Dozvoljeno je odstupanje +- 5% ● Boja metalne konstrukcije: RAL 7035. | AO1 - ARCHIVE CABINET - 92x42x195cm ● Procurement and delivery of metal archive cabinets. They are made of high-quality sheet steel of the appropriate thickness. The cabinets have double doors with a large opening angle and movable shelves inside them. The load capacity of the shelf is 50 kg. The cabinet doors have a high-quality cylinder lock with a three-way closing mechanism. ● A deviation of +/- 5% is allowed ● Color of the metal structure: RAL 7035. | kom/pcs |  | 35 | 0
3. |  | V1 - VJEŠAONIK - 40x175.5cm ● Nabavka i isporuka vješaonika izrađenog od kombinacije materijala: metal - drvo - MDF. Bijele je boje, ima šest kuka za kačenje odjeće koje su postavljene asimetrično. Prečnik kružne baze vješaonika je 40cm, dok je njegova ukupna visina 175.5cm. ● Dozvoljeno je odstupanje +- 5% | V1 -HANGER - 40x175.5cm ● Procurement and delivery of the hanger made of a combination of metal - wood - MDF. It is white and has six hooks for hanging clothes placed asymmetrically. The diameter of the circular base of the hanger is 40 cm, while its total height is 175.5 cm. ● A deviation of +/- 5% is allowed | kom/pcs |  | 15 | 0
4. |  | KST1 - KANCELARIJSKA STOLICA - 48x70x113-121cm ● Nabavka i isporuka kancelarijske stolice - visokokvalitetne radne fotelje - koja ima bazu od inoksa, dok mehanizam fotelje omogućava podešavanje sjedišta i naslona. Nasloni za ruke su fiksni, zaobljeni, od hromiranog čelika sa obloženim gornjim dijelom. I sama stolica i prethodno pomenuti nasloni za ruke, obloženi su štofom u crnoj boji. Baza od pet krakova izrađena od aluminijuma sa točkićima za piruetiranje sa dvostrukim gaznim slojem. Širina stolice je 48cm, dužina 70cm, a visina stolice 113-121cm. Visina sjedišta stolice: 42-50cm. ● Dozvoljeno je odstupanje +- 5% | KST1 - OFFICE CHAIR - 48x70x113-121cm ● Procurement and delivery of the office chair - a high-quality work chair - made of stainless steel, while the chair mechanism allows the seat and backrest to be adjusted. The armrests are fixed, rounded, and made of chromed steel with a coated upper part. The chair and the armrests are covered with black textiles. Five-spoke base made of aluminium with double-tread pirouette wheels. The chair's width is 48 cm, the length is 70 cm, and the height is 113-121 cm. Chair seat height: 42-50cm. ● A deviation of +/- 5% is allowed | kom/pcs |  | 16 | 0
5. |  | KST2 - KONFERENCIJSKA STOLICA-47x43x83cm ● Nabavka i isporuka konferencijske stolice koja ima tapacirano sjedište i naslon, metalni hromirani okvir, plastičnu oblogu donjeg dijela sjedišta i naslona i čija je nosivost 120 kg. Boja štofa kojim je tapacirano sjedište stolice, kao i naslon je crna. Širina sjedišta je 47cm, dubina 43cm, a ukupna visina stolice 83cm. Visina sjedišta je 49cm. ● Dozvoljeno je odstupanje +- 5% | KST2 - CONFERENCE CHAIR - 47x43x83cm ● Procurement and delivery of the conference chair with an upholstered seat and backrest, a metal chrome frame, plastic covering of the lower part of the seat and backrest, and a load capacity of 120 kg. The colour of the textil used to upholster the seat of the chair and the backrest, is black. The width of the seat is 47 cm, the depth is 43 cm, and the total height of the chair is 83 cm. Seat height is 49cm. ● A deviation of +/- 5% is allowed | kom/pcs |  | 149 | 0
6. |  | ŠK1 - ŠKOLSKA KLUPA (dvosjed) - 130x50x75cm ● Nabavka i isporuka školskih klupa (dvosjeda), čija je konstrukcija izrađena od cijevi okruglog presjeka Ø25mm, debljine zida 1.50mm, dok je ploča klupe, dimenzija 130x50cm, izrađena od univera debljine 18mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Klupa ima i kukice za rančeve sa strane. ● Boja metalne konstrukcije: RAL 9010. ● Nogari stola su zaštićeni plastičnim čepovima. ● Dozvoljeno je odstupanje +- 5% | ŠK1 - SCHOOL BENCH (two-seater) - 130x50x75cm ● Procurement and delivery of school benches (two-seaters), the construction of which is made of a pipe with a round section of Ø25mm and the wall thickness of 1.50mm. In addition, the bench top, with dimensions of 130x50cm, is made of 18mm thick particle board, coated with white melamine foil and whose sides are treated with polyurethane bucket and glued with PU glue. The bench also has hooks for backpacks on the side. ● Metal construction colour: RAL 9010. ● Table legs are protected with plastic plugs. ● A deviation of +/- 5% is allowed | kom/pcs |  | 369 | 0
7. |  | ŠK2 - ŠKOLSKA KLUPA (dvosjed) - 130x60x75cm ● Nabavka i isporuka školskih klupa (dvosjeda), čija je konstrukcija izrađena od cijevi okruglog presjeka Ø25mm, debljine zida 1.50mm, dok je ploča klupe, dimenzija 130x60cm, izrađena od univera debljine 18mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Klupa ima i kukice za rančeve sa strane. ● Boja metalne konstrukcije: RAL 9010. ● Nogari stola su zaštićeni plastičnim čepovima. ● Dozvoljeno je odstupanje +- 5% | ŠK2 - SCHOOL BENCH (two-seater) - 130x60x75cm ● Procurement and delivery of school benches (two-seaters), the construction of which is made of a pipe with a round section of Ø25mm and the wall thickness of 1.50mm. In addition, the bench top, with dimensions of 130x60cm, is made of 18mm thick particle board, coated with white melamine foil and whose sides are treated with polyurethane bucket and glued with PU glue. The bench also has hooks for backpacks on the side. ● Metal construction colour: RAL 9010. ● Table legs are protected with plastic plugs. ● A deviation of +/- 5% is allowed | kom/pcs |  | 60 | 0
8. |  | ŠK3 - ŠKOLSKA KLUPA (dvosjed) - 120x60x75cm ● Nabavka i isporuka školskih klupa (dvosjeda), čija je konstrukcija izrađena od cijevi okruglog presjeka Ø25mm, debljine zida 1.50mm, dok je ploča klupe, dimenzija 120x60cm, izrađena od univera debljine 18mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Klupa ima i kukice za rančeve sa strane. ● Boja metalne konstrukcije: RAL 9010. ● Nogari stola su zaštićeni plastičnim čepovima. ● Dozvoljeno je odstupanje +- 5% | ŠK3 - SCHOOL BENCH (two-seater) - 120x60x75cm ● Procurement and delivery of school benches (two-seaters), the construction of which is made of pipes with a round section Ø25mm, the wall thickness of 1.50mm. In addition, the bench top, dimensions 120x60cm, is made of 18mm thick particle board, which is covered with white melamine foil and whose sides are treated with polyurethane buckets and glued with PU glue. The bench also has hooks for backpacks on the side. ● Metal construction colour: RAL 9010. ● Table legs are protected with plastic plugs. ● A deviation of +/- 5% is allowed | kom/pcs |  | 13 | 0
9. |  | ŠST1 - ŠKOLSKA STOLICA - H 46cm ● Nabavka i isporuka školskih stolica, čija je konstrukcija izrađena od cijevi okruglog presjeka Ø22mm, debljine zida 1.50mm, dok su sjedište i naslon izrađeni od bukovog spera debljine 9mm, lakiranog PU lakom. Dimenzije naslova: 35x20cm; dimenzije sjedišta: 35x37cm. Visina sjedišta je 46cm. ● Boja metalne konstrukcije: RAL 9010. ● Nogari stolice su zaštićeni plastičnim čepovima. ● Dozvoljeno je odstupanje +- 5% | ŠST1 - SCHOOL CHAIR - H 46cm ● Procurement and delivery of school chairs, the construction of which is made of a tube with a round section Ø22mm, wall thickness 1.50mm, while the seat and back are made of beech plywood 9mm thick, varnished with PU varnish. Dimensions of the title: 35x20cm; measurements of the seat: 35x37cm. Height seat length is 46cm. ● Metal construction colour: RAL 9010. ● Plastic plugs protect the legs of the chair. ● A deviation of +/- 5% is allowed | kom/pcs |  | 869 | 0
10. |  | NS1 - ŠKOLSKA KATEDRA (NASTAVNIČKI STO) - 130x60x75cm ● Nabavka i isporuka školskih katedri, čija je konstrukcija izrađena od cijevi okruglog presjeka Ø25mm, debljine zida 1.50mm. Ploča, leđa i fioke izrađeni su od univera debljine 18mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Katedra posjeduje dvije fioke sa desne strane. ● Boja metalne konstrukcije: RAL 9010. ● Nogari katedre su zaštićeni plastičnim čepovima. ● Dozvoljeno je odstupanje +- 5% | NS1 - SCHOOL DESK (TEACHER'S DESK - 130x60x75cm ● Procurement and delivery of teacher's desks, the construction of pipes with a round section Ø25mm, the wall thickness of 1.50mm. The top, back and drawers are made of 18mm thick particle board, covered with white melamine foil and whose sides are treated with polyurethane edging and glued with PU glue. The desk has two drawers on the right side. ● Metal construction colour: RAL 9010. ● Plastic caps protect the legs of the chair. ● A deviation of +/- 5% is allowed | kom/pcs |  | 25 | 0
11. |  | NST1 - NASTAVNIČKA STOLICA - 47x43x83cm ● Nabavka i isporuka nastavničke stolice koja ima tapacirano sjedište i naslon, metalni hromirani okvir, plastičnu oblogu donjeg dijela sjedišta i naslona i čija je nosivost 120 kg. Boja štofa kojim je tapacirano sjedište stolice, kao i naslon je crna. Širina sjedišta je 47cm, dubina 43cm, a ukupna visina stolice 83cm. Visina sjedišta je 49cm. ● Dozvoljeno je odstupanje +- 5% | NST1 - TEACHER'S CHAIR - 47x43x83cm ● Procurement and delivery of a teacher's chair with an upholstered seat and backrest, a metal chrome frame, a plastic coating on the seat and backrest, and a load capacity of 120 kg. The colour of the textile used to upholster the seat of the chair, as well as the backrest, is black. The width of the seat is 47cm, the depth is 43cm, and the total height of the chair is 83cm. The height of the seat is 49cm. ● A deviation of +/- 5% is allowed | kom/pcs |  | 29 | 0
12. |  | KS3 - KONFERENCIJSKI STO - Ø 80cm ● Nabavka i isporuka konferencijskog stola prečnika Ø 80cm, visine 75cm. Baza stola je kružna - Ø 45cm, metalna, hromirana. Istog materijala je i stub stola. Ploča stola je HPL ploča, debljine 10mm, sa zakošenim donjim ivicama. Boja ploče je bijela - RAL 9010. ● Dozvoljeno je odstupanje +- 5% | KS3 - CONFERENCE TABLE - Ø 80cm ● Procurement and delivery of the conference table diameter Ø 80cm, height 75cm. The base of the table is circular - Ø 45cm, metal, chromed. The table post is made of the same material. The table top is an HPL board, 10 mm thick, with bevelled lower edges. The colour of the plate is white - RAL 9010. ● A deviation of +/- 5% is allowed | kom/pcs |  | 1 | 0
13. |  | ŠTZ1 - ŠKOLSKA TABLA ZELENA - 240x120cm ● Nabavka i isporuka zelene školske table za pisanje kredom, koja posjeduju aluminijski ram i metalne nosače. Visina table je 120cm, a širina 240cm. | ŠTZ1 - SCHOOL BOARD GREEN - 240x120cm ● Procurement and delivery of a green school board for writing with chalk, with the aluminium frame and metal supports. The height of the board is 120cm, and the width is 240cm. | kom/pcs |  | 29 | 0
14. |  | F1 - FOTELJA - 96x97x82cm ● Nabavka i isporuka fotelje modernog dizajna, sa drvenim nogarima. Presvučena je štofom u sivoj boji. Fotelja se ne rasklapa. Predviđene dimenzije su 96x97x82cm. ● Dozvoljeno je odstupanje +- 5% | F1 - ARMCHAIR - 96x97x82cm ● Procurement and delivery of an armchair of modern design, with wooden legs. It is covered with the textile in grey colour. The armchair does not fold. The estimated dimensions are96x97x82cm. ● A deviation of +/- 5% is allowed | kom/pcs |  | 6 | 0
15. |  | T1 - TROSJED - 245x97x82cm ● Nabavka i isporuka trosjeda modernog dizajna, sa drvenim nogarima. Presvučen je štofom u sivoj boji. Trosjed se ne rasklapa. Širine je 245cm, dubine 97cm i visine 82cm. ● Dozvoljeno je odstupanje +- 5% | T1 - THREE-SEATER - 245x97x82cm ● Procurement and delivery of three-seaters of modern design with wooden legs. It is covered with the textile in grey colour. The sofa does not fold. It is 245 cm wide, 97 cm deep and 82 cm high. ● A deviation of +/- 5% is allowed | kom/pcs |  | 4 | 0
16. |  | TS1 - TRPEZARIJSKI STO ● Nabavka i isporuka trpezarijskog stola prečnika 80cm. Ploča stola je bijele boje, sa zaobljenim ivicama. Sto ima drvene nogare. ● Dozvoljeno je odstupanje +- 5% | TS1 - DINING TABLE ● Procurement and delivery of the dining table with a diameter of 80 cm. The table top is white, with rounded edges. The table has wooden legs. ● A deviation of +/- 5% is allowed | kom/pcs |  | 6 | 0
17. |  | STL1 - STOLICA ● Nabavka i isporuka stolica kod kojih je sjedište, odnosno naslon u bijeloj boji i koje imaju drvene nogare. ● Dozvoljeno je odstupanje +- 5% | STL1 - CHAIR ● Procurement and delivery of chairs with a white seat, backrest, and wooden legs. ● A deviation of +/- 5% is allowed | kom/pcs |  | 28 | 0
I. |  | SERIJSKA OPREMA | SERIAL EQUIPMENT |  |  | Ukupno/ Total | 0
II. |  | NAMJEŠTAJ PO MJERI | CUSTOM FURNITURE
18. |  | KLS1 - KLUB STO - 120x60x40cm ● Izrada i isporuka klub stola čija je konstrukcija izrađena od kutije prečnika 20x20mm, a ploča od dvije spojene univer ploče debljine 18mm, koje su presvučene bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Metalni dio stola je završno bojen u bijelo. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | KLS1 - THE CLUB TABLE - 120x60x40cm ● Production and delivery of the club table, the structure is made of a box with dimensions of 20x20mm and the plate is made of two plates of particle boards, 18mm thick, which are covered with white melamine foil and whose sides are treated with polyurethane edges, and glued with PU adhesive. The metal part of the table is painted white. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 4 | 0
19. |  | RS1 - RADNI STO - 150x70x75cm ● Izrada i isporuka radnog stola izrađenog od univera debljine 18mm. Ploču stola čine dvije spojene univer ploče debljine 18mm, koje su presvučene bijelom melaminskom folijom i čije su strane obrađene poliuretanskim kantovima, a lijepljene PU lijepkom. Na isti način izrađene su i bočne strane stola. Na zadnjoj strani, sto je ojačan duplom univerom pločom debljine 18mm. Sto posjeduje i rozetu za provlačenje kablova (Ø 60mm). ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | RS1 - WORK TABLE - 150x70x75cm ● Production and delivery of an 18mm thick particle board work table. The table top consists of two 18mm thick particle boards, which are covered with white melamine foil and whose sides are treated with polyurethane edges and glued with PU adhesive. The sides are also made in the same way table. On the back side, the table is reinforced with a double particle boards with a thickness of 18 mm. The table also has a rosette for passing cables (Ø 60 mm). ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 14 | 0
20. |  | RS2 - RADNI STO - 204x60x75cm ● Izrada i isporuka radnog stola izrađenog od univera debljine 18mm. Ploču stola čine dvije spojene univer ploče debljine 18mm, koje su presvučene bijelom melaminskom folijom i čije su strane obrađene poliuretanskim kantovima, a lijepljene PU lijepkom. Na isti način izrađene su i bočne strane stola. Na zadnjoj strani, sto je ojačan duplom univer pločom debljine 18mm. Sto posjeduje i rozetu za provlačenje kablova. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | RS2 - WORK TABLE - 204x60x75cm ● Production and delivery of an 18mm thick particle board work table. The table top consists of two 18mm thick particle boards, which are covered with white melamine foil and whose sides are treated with polyurethane edges and glued with PU adhesive. The sides are also made in the same way table. On the back side, the table is reinforced with a double particlel board with a thickness of 18 mm. The table also has a rosette for passing cables. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 1 | 0
21. |  | RS3 - RADNI STO - 180x80x75cm ● Izrada i isporuka radnog stola izrađenog od univera debljine 18mm. Ploču stola čine dvije spojene univer ploče debljine 18mm, koje su presvučene bijelom melaminskom folijom i čije su strane obrađene poliuretanskim kantovima, a lijepljene PU lijepkom. Na zadnjoj strani, sto je ojačan duplom univer pločom debljine 18mm. Sto posjeduje i rozetu za provlačenje kablova. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | RS3 - WORK TABLE - 180x80x75cm ● Production and delivery of an 18mm thick particle board work table. The table top consists of two 18mm thick particle boards, which are covered with white melamine foil and whose sides are treated with polyurethane edges and glued with PU adhesive. The sides are also made in the same way table. On the back side, the table is reinforced with a double universal board with a thickness of 18 mm. The table also has a rosette for passing cables. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 2 | 0
22. |  | KS1 - KONFERENCIJSKI STO - 150x80x75cm ● Izrada i isporuka konferencijskog stola izrađenog od univera debljine 18mm. Ploču stola čine dvije spojene univer ploče debljine 18mm, koje su presvučene bijelom melaminskom folijom i čije su strane obrađene poliuretanskim kantovima, a lijepljene PU lijepkom. Na isti način izrađene su i bočne strane stola. Po sredini, sto je ojačan duplom univer-pločom debljine 18mm. Sto posjeduje i dvije rozetne za provlačenje kablova. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | KS1 - CONFERENCE TABLE - 150x80x75cm ●Production and delivery of a conference table of 18mm thick particle board. The table top consists of two joined 18mm thick particle boards coated with white melamine foil and whose sides are treated with polyurethane edges and glued with PU glue. The sides are also made in the same way. In the middle, the table is reinforced with double particle boards 18 mm thick. The table also has two rosettes for passing cables. ● Check all measures on the spot. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 8 | 0
23. |  | KS2 - KONFERENCIJSKI STO - 150x100x75cm ● Izrada i isporuka konferencijskog stola izrađenog od univera debljine 18mm. Ploču stola čine dvije spojene univer ploče debljine 18mm, koje su presvučene bijelom melaminskom folijom i čije su strane obrađene poliuretanskim kantovima, a lijepljene PU lijepkom. Na isti način izrađene su i bočne strane stola. Po sredini, sto je ojačan duplom univer pločom debljine 18mm. Sto posjeduje i dvije rozetne za provlačenje kablova. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | KS2 - CONFERENCE TABLE - 150x100x75cm ●Production and delivery of a conference table of 18mm thick particle board. The table top consists of two joined 18mm thick particle boards coated with white melamine foil and whose sides are treated with polyurethane edges and glued with PU glue. The sides are also made in the same way. In the middle, the table is reinforced with double particle boards 18 mm thick. The table also has two rosettes for passing cables. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 17 | 0
24. |  | DS1 - DEMONSTRACIONI STO - 200x70x75cm ● Izrada i isporuka demonstracionih stolova izrađenih od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sto je presvučen folijom otpornom na hemikalije, a sadrži kadicu 40/40cm sa slavinom za hladnu vodu, takođe otpornu na hemikalije, kao i priključak za struju i ormariće i fioke. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | DS1 - DEMONSTRATION TABLE - 200x70x75cm ● Production and delivery of demonstration tables made of 18mm and 25mm thick particle board covered with white melamine foil and whose sides are treated with polyurethane edging and glued with PU glue. The table is covered with chemical-resistant foil and contains a 40/40cm tub with a tap for cold water, also resistant to chemicals, and an electrical connection and cabinets and drawers. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 4 | 0
25. |  | S1 - STO - 80x80x75cm ● Izrada i isporuka stola izrađenog od univera debljine 18mm. Ploču stola čine dvije spojene univer ploče debljine 18mm, koje su presvučene bijelom melaminskom folijom i čije su strane obrađene poliuretanskim kantovima, a lijepljene PU lijepkom. Na isti način izrađene su i bočne strane stola. Po sredini, sto je ojačan duplom univer-pločom debljine 18mm. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | S1 -TABLE - 80x80x75cm ● Production and delivery of a table of 18mm thick particle board. The table top consists of two 18mm thick particle boards, which are covered with white melamine foil and whose sides are treated with polyurethane edges and glued with PU adhesive. The sides of the table are made in the same way. In the middle, the table is reinforced with a double particle board 18 mm thick. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 3 | 0
26. |  | S2 - STO - 160x80x75cm ● Izrada i isporuka stola izrađenog od univera debljine 18mm. Ploču stola čine dvije spojene univer ploče debljine 18mm, koje su presvučene bijelom melaminskom folijom i čije su strane obrađene poliuretanskim kantovima, a lijepljene PU lijepkom. Na isti način izrađene su i bočne strane stola. Po sredini, sto je ojačan duplom univer-pločom debljine 18mm. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | S2 - TABLE - 160x80x75cm ● Production and delivery of a table of 18mm thick particle board. The table top consists of two 18mm thick particle boards, which are covered with white melamine foil and whose sides are treated with polyurethane edges and glued with PU adhesive. The sides of the table are made in the same way. In the middle, the table is reinforced with a double particle board 18 mm thick. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 4 | 0
27. |  | S3 - STO - 280x80x75cm ● Izrada i isporuka stola izrađenog od univera debljine 18mm. Ploču stola čine dvije spojene univer ploče debljine 18mm, koje su presvučene bijelom melaminskom folijom i čije su strane obrađene poliuretanskim kantovima, a lijepljene PU lijepkom. Na isti način izrađene su i bočne strane stola. Po sredini, sto je ojačan duplom univer-pločom debljine 18mm. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | S3 - TABLE - 280x80x75cm ● Production and delivery of a table of 18mm thick particle board. The table top consists of two 18mm thick particle boards, which are covered with white melamine foil and whose sides are treated with polyurethane edges and glued with PU adhesive. The sides of the table are made in the same way. In the middle, the table is reinforced with a double particle board 18 mm thick. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 2 | 0
28. |  | P1 - PLAKAR - 371.5x40x318cm ● Izrada i isporuka plakara koji je izrađen od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na plakaru opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). Iznad samog plakara, odnosno dijela za skladištenje i odlaganje stvari, univerom debljine 18mm i 25mm napravljena je "maska" s ciljem popunjavanja prostora iznad plakara, do plafona, a ista služi i za kačenje panoa, plakata i sl. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | P1 - CABINET - 371.5x40x318cm ● Production and delivery of a cabinet made of 18mm and 25mm thick particle boards coated with white melamine foil. The sides are treated with polyurethane edging and glued with PU adhesive. All doors on the cabinet have the handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). Above the cabinet, i.e. the part for storing things, a "mask" was made with 18mm and 25mm thick particle boards to fill the space up to the ceiling, and it is also used for hanging panels, posters, etc. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 3 | 0
29. |  | P2 - PLAKAR - 364x40x318cm ● Izrada i isporuka plakara koji je izrađen od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na plakaru opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). Iznad samog plakara, odnosno dijela za skladištenje i odlaganje stvari, univerom debljine 18mm i 25mm napravljena je "maska" s ciljem popunjavanja prostora iznad plakara, do plafona, a ista služi i za kačenje panoa, plakata i sl. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | P2 - CABINET - 364x40x318cm ● Production and delivery of a cabinet made of 18mm and 25mm thick particle boards coated with white melamine foil. The sides are treated with polyurethane edging and glued with PU adhesive. All doors on the cabinet have the handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). Above the cabinet, i.e. the part for storing things, a "mask" was made with 18mm and 25mm thick particle boards to fill the space up to the ceiling, and it is also used for hanging panels, posters, etc. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 14 | 0
30. |  | P3 - PLAKAR - 351x40x318cm ● Izrada i isporuka plakara koji je izrađen od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na plakaru opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). Iznad samog plakara, odnosno dijela za skladištenje i odlaganje stvari, univerom debljine 18mm i 25mm napravljena je "maska" s ciljem popunjavanja prostora iznad plakara, do plafona, a ista služi i sa kačenje panoa, plakata i sl. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | P3 - CABINET - 351x40x318cm ● Production and delivery of a cabinet made of 18mm and 25mm thick particle boards coated with white melamine foil. The sides are treated with polyurethane edging and glued with PU adhesive. All doors on the cabinet have the handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). Above the cabinet, i.e. the part for storing things, a "mask" was made with 18mm and 25mm thick particle boards to fill the space up to the ceiling, and it is also used for hanging panels, posters, etc. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 5 | 0
31. |  | P4 - PLAKAR - 72x40x318cm ● Izrada i isporuka plakara koji je izrađen od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na plakaru opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). Iznad samog plakara, odnosno dijela za skladištenje i odlaganje stvari, univerom debljine 18mm i 25mm napravljena je "maska" s ciljem popunjavanja prostora iznad plakara, do plafona, a ista služi i za kačenje panoa, plakata i sl. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | P4 -CABINET - 72x40x318cm ● Production and delivery of a cabinet made of 18mm and 25mm thick particle boards coated with white melamine foil. The sides are treated with polyurethane edging and glued with PU adhesive. All doors on the cabinet have the handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). Above the cabinet, i.e. the part for storing things, a "mask" was made with 18mm and 25mm thick particle boards to fill the space up to the ceiling, and it is also used for hanging panels, posters, etc. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 1 | 0
32. |  | P5 - PLAKAR - 311x40x318cm ● Izrada i isporuka plakara koji je izrađen od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na plakaru opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). Iznad samog plakara, odnosno dijela za skladištenje i odlaganje stvari, univerom debljine 18mm i 25mm napravljena je "maska" s ciljem popunjavanja prostora iznad plakara, do plafona. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | P5 - CABINET - 311x40x318cm ● Production and delivery of a cabinet made of 18mm and 25mm thick particle boards coated with white melamine foil. The sides are treated with polyurethane edging and glued with PU adhesive. All doors on the cabinet have the handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). Above the cabinet, i.e. the part for storing things, a "mask" was made with 18mm and 25mm thick particle boards to fill the space up to the ceiling, and it is also used for hanging panels, posters, etc. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 1 | 0
33. |  | P6 - PLAKAR - 350.5x40x318cm ● Izrada i isporuka plakara koji je izrađen od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na plakaru opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). Iznad samog plakara, odnosno dijela za skladištenje i odlaganje stvari, univerom debljine 18mm i 25mm napravljena je "maska" s ciljem popunjavanja prostora iznad plakara, do plafona, a ista služi i za kačenje panoa, plakata i sl. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | P6 -CABINET - 350.5x40x318cm ● Production and delivery of a cabinet made of 18mm and 25mm thick particle boards coated with white melamine foil. The sides are treated with polyurethane edging and glued with PU adhesive. All doors on the cabinet have the handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). Above the cabinet, i.e. the part for storing things, a "mask" was made with 18mm and 25mm thick particle boards to fill the space up to the ceiling, and it is also used for hanging panels, posters, etc. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 3 | 0
34. |  | P7 - PLAKAR - 250x35x318cm ● Izrada i isporuka plakara koji je izrađen od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na plakaru opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). Ovaj tip plakara osim zatvorenih i otvorenih polica sadrži i prostor za skladištenje u fiokama. Iznad samog plakara, odnosno dijela za skladištenje i odlaganje stvari, univerom debljine 18mm i 25mm napravljena je "maska" s ciljem popunjavanja prostora iznad plakara, do plafona, a ista služi i za kačenje panoa, plakata i sl. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | P7 - CABINET - 250x35x318cm ● Production and delivery of a cabinet made of 18mm and 25mm thick particle boards coated with white melamine foil. The sides are treated with polyurethane edging and glued with PU adhesive. All doors on the cabinet have the handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). In addition to closed and open shelves, this type of cabinet also contains space for storage in drawers Above the cabinet, i.e. the part for storing things, a "mask" was made with 18mm and 25mm thick particle boards to fill the space up to the ceiling, and it is also used for hanging panels, posters, etc. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 1 | 0
35. |  | P8 - PLAKAR - 192x60x290cm ● Izrada i isporuka plakara koji je izrađen od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na plakaru opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). Iznad samog plakara, odnosno dijela za skladištenje i odlaganje stvari, univerom debljine 18mm i 25mm napravljena je "maska" s ciljem popunjavanja prostora iznad plakara, do plafona. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | P8 - CABINET - 192x60x290cm ● Production and delivery of a cabinet made of 18mm and 25mm thick particle boards coated with white melamine foil. The sides are treated with polyurethane edging and glued with PU adhesive. All doors on the cabinet have the handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). Above the cabinet, i.e. the part for storing things, a "mask" was made with 18mm and 25mm thick particle boards to fill the space up to the ceiling, and it is also used for hanging panels, posters, etc. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 2 | 0
36. |  | P9 - PLAKAR - 222x35x318cm ● Izrada i isporuka plakara koji je izrađen od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na plakaru opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). Iznad samog plakara, odnosno dijela za skladištenje i odlaganje stvari, univerom debljine 18mm i 25mm napravljena je "maska" s ciljem popunjavanja prostora iznad plakara, do plafona, a ista služi i za kačenje panoa, plakata i sl. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | P9 - CABINET - 222x35x318cm ● Production and delivery of a cabinet made of 18mm and 25mm thick particle boards coated with white melamine foil. The sides are treated with polyurethane edging and glued with PU adhesive. All doors on the cabinet have the handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). Above the cabinet, i.e. the part for storing things, a "mask" was made with 18mm and 25mm thick particle boards to fill the space up to the ceiling, and it is also used for hanging panels, posters, etc. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 1 | 0
37. |  | P10 - PLAKAR - 74x40x318cm ● Izrada i isporuka plakara koji je izrađen od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na plakaru opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). Iznad samog plakara, odnosno dijela za skladištenje i odlaganje stvari, univerom debljine 18mm i 25mm napravljena je "maska" s ciljem popunjavanja prostora iznad plakara, do plafona, a ista služi i za kačenje panoa, plakata i sl. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | P10 - CABINET - 74x40x318cm ● Production and delivery of a cabinet made of 18mm and 25mm thick particle boards coated with white melamine foil. The sides are treated with polyurethane edging and glued with PU adhesive. All doors on the cabinet have the handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). Above the cabinet, i.e. the part for storing things, a "mask" was made with 18mm and 25mm thick particle boards to fill the space up to the ceiling, and it is also used for hanging panels, posters, etc. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 1 | 0
38. |  | P11 - PLAKAR - 400x40x318cm ● Izrada i isporuka plakara koji je izrađen od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na plakaru opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). Ovaj tip plakara osim zatvorenih i otvorenih polica sadrži i prostor za skladištenje u fiokama. Iznad samog plakara, odnosno dijela za skladištenje i odlaganje stvari, univerom debljine 18mm i 25mm napravljena je "maska" s ciljem popunjavanja prostora iznad plakara, do plafona, a ista služi i za kačenje panoa, plakata i sl. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | P11 -CABINET - 400x40x318cm ● Production and delivery of a cabinet made of 18mm and 25mm thick particle boards coated with white melamine foil. The sides are treated with polyurethane edging and glued with PU adhesive. All doors on the cabinet have the handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). In addition to closed and open shelves, this type of cabinet also contains space for storage in drawers Above the cabinet, i.e. the part for storing things, a "mask" was made with 18mm and 25mm thick particle boards to fill the space up to the ceiling, and it is also used for hanging panels, posters, etc. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 4 | 0
39. |  | P12 - PLAKAR - 130x35x318cm ● Izrada i isporuka plakara koji je izrađen od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na plakaru opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). Iznad samog plakara, odnosno dijela za skladištenje i odlaganje stvari, univerom debljine 18mm i 25mm napravljena je "maska" s ciljem popunjavanja prostora iznad plakara, do plafona, ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | P12 - CABINET - 130x35x318cm ● Production and delivery of a cabinet made of 18mm and 25mm thick particle boards coated with white melamine foil. The sides are treated with polyurethane edging and glued with PU adhesive. All doors on the cabinet have the handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). Above the cabinet, i.e. the part for storing things, a "mask" was made with 18mm and 25mm thick particle boards to fill the space up to the ceiling, and it is also used for hanging panels, posters, etc. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 2 | 0
40. |  | P13 - PLAKAR - 140x35x318cm ● Izrada i isporuka plakara koji je izrađen od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na plakaru opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). Iznad samog plakara, odnosno dijela za skladištenje i odlaganje stvari, univerom debljine 18mm i 25mm napravljena je "maska" s ciljem popunjavanja prostora iznad plakara, do plafona, ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | P13 - CABINET - 140x35x318cm ● Production and delivery of a cabinet made of 18mm and 25mm thick particle boards coated with white melamine foil. The sides are treated with polyurethane edging and glued with PU adhesive. All doors on the cabinet have the handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). Above the cabinet, i.e. the part for storing things, a "mask" was made with 18mm and 25mm thick particle boards to fill the space up to the ceiling, and it is also used for hanging panels, posters, etc. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 1 | 0
41. |  | P14 - PLAKAR - 250x40x318cm ● Izrada i isporuka plakara koji je izrađen od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na plakaru opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). Ovaj tip plakara osim zatvorenih i otvorenih polica sadrži i prostor za skladištenje u fiokama. Iznad samog plakara, odnosno dijela za skladištenje i odlaganje stvari, univerom debljine 18mm i 25mm napravljena je "maska" s ciljem popunjavanja prostora iznad plakara, do plafona. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | P14 -CABINET - 250x40x318cm ● Production and delivery of a cabinet made of 18mm and 25mm thick particle boards coated with white melamine foil. The sides are treated with polyurethane edging and glued with PU adhesive. All doors on the cabinet have the handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). In addition to closed and open shelves, this type of cabinet also contains space for storage in drawers Above the cabinet, i.e. the part for storing things, a "mask" was made with 18mm and 25mm thick particle boards to fill the space up to the ceiling, and it is also used for hanging panels, posters, etc. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 1 | 0
42. |  | P15 - PLAKAR - 240x35x120cm ● Izrada i isporuka plakara koji je izrađen od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na plakaru opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). Ovaj tip plakara osim zatvorenih i otvorenih polica sadrži i prostor za skladištenje u fiokama. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | P15 - CABINET - 240x35x120cm ● Production and delivery of a cabinet made of 18mm and 25mm thick particle boards coated with white melamine foil. The sides are treated with polyurethane edging and glued with PU adhesive. All doors on the cabinet have the handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). In addition to closed and open shelves, this type of cabinet also contains space for storage in drawers ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 2 | 0
43. |  | P16 - PLAKAR - 180x35x318cm ● Izrada i isporuka plakara koji je izrađen od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na plakaru opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). Iznad samog plakara, odnosno dijela za skladištenje i odlaganje stvari, univerom debljine 18mm i 25mm napravljena je "maska" s ciljem popunjavanja prostora iznad plakara, do plafona, a ista služi i sa kačenje panoa, plakata i sl. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | P16 -CABINET - 180x35x318cm ● Production and delivery of a cabinet made of 18mm and 25mm thick particle boards coated with white melamine foil. The sides are treated with polyurethane edging and glued with PU adhesive. All doors on the cabinet have the handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). Above the cabinet, i.e. the part for storing things, a "mask" was made with 18mm and 25mm thick particle boards to fill the space up to the ceiling, and it is also used for hanging panels, posters, etc. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 3 | 0
44. |  | P17 - PLAKAR - 324x40x318cm ● Izrada i isporuka plakara koji je izrađen od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na plakaru opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). Ovaj tip plakara osim zatvorenih i otvorenih polica sadrži i prostor za skladištenje u fiokama. Iznad samog plakara, odnosno dijela za skladištenje i odlaganje stvari, univerom debljine 18mm i 25mm napravljena je "maska" s ciljem popunjavanja prostora iznad plakara, do plafona, a ista služi i za kačenje panoa, plakata i sl. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | P17 - PLAKAR - 324x40x318cm ● Production and delivery of a cabinet made of 18mm and 25mm thick particle boards coated with white melamine foil. The sides are treated with polyurethane edging and glued with PU adhesive. All doors on the cabinet have the handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). In addition to closed and open shelves, this type of cabinet also contains space for storage in drawers Above the cabinet, i.e. the part for storing things, a "mask" was made with 18mm and 25mm thick particle boards to fill the space up to the ceiling, and it is also used for hanging panels, posters, etc. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 2 | 0
45. |  | P18 - PLAKAR - 354x40x318cm ● Izrada i isporuka plakara koji je izrađen od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na plakaru opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). Iznad samog plakara, odnosno dijela za skladištenje i odlaganje stvari, univerom debljine 18mm i 25mm napravljena je "maska" s ciljem popunjavanja prostora iznad plakara, do plafona, a ista služi i sa kačenje panoa, plakata i sl. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | P18 - CABINET - 354x40x318cm ● Production and delivery of a cabinet made of 18mm and 25mm thick particle boards coated with white melamine foil. The sides are treated with polyurethane edging and glued with PU adhesive. All doors on the cabinet have the handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). Above the cabinet, i.e. the part for storing things, a "mask" was made with 18mm and 25mm thick particle boards to fill the space up to the ceiling, and it is also used for hanging panels, posters, etc. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 1 | 0
46. |  | P19 - PLAKAR - 71.5x40x318cm ● Izrada i isporuka plakara koji je izrađen od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na plakaru opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). Iznad samog plakara, odnosno dijela za skladištenje i odlaganje stvari, univerom debljine 18mm i 25mm napravljena je "maska" s ciljem popunjavanja prostora iznad plakara, do plafona, a ista služi i sa kačenje panoa, plakata i sl. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | P19 - CABINET - 71.5x40x318cm ● Production and delivery of a cabinet made of 18mm and 25mm thick particle boards coated with white melamine foil. The sides are treated with polyurethane edging and glued with PU adhesive. All doors on the cabinet have the handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). Above the cabinet, i.e. the part for storing things, a "mask" was made with 18mm and 25mm thick particle boards to fill the space up to the ceiling, and it is also used for hanging panels, posters, etc. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 1 | 0
47. |  | P20 - PLAKAR - 218x40x318cm ● Izrada i isporuka plakara koji je izrađen od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na plakaru opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). Iznad samog plakara, odnosno dijela za skladištenje i odlaganje stvari, univerom debljine 18mm i 25mm napravljena je "maska" s ciljem popunjavanja prostora iznad plakara, do plafona, a ista služi i za kačenje panoa, plakata i sl. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | P20 -CABINET - 218x40x318cm ● Production and delivery of a cabinet made of 18mm and 25mm thick particle boards coated with white melamine foil. The sides are treated with polyurethane edging and glued with PU adhesive. All doors on the cabinet have the handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). Above the cabinet, i.e. the part for storing things, a "mask" was made with 18mm and 25mm thick particle boards to fill the space up to the ceiling, and it is also used for hanging panels, posters, etc. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 4 | 0
48. |  | P21 - PLAKAR - 67x40x318cm ● Izrada i isporuka plakara koji je izrađen od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na plakaru opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). Iznad samog plakara, odnosno dijela za skladištenje i odlaganje stvari, univerom debljine 18mm i 25mm napravljena je "maska" s ciljem popunjavanja prostora iznad plakara, do plafona, a ista služi i sa kačenje panoa, plakata i sl. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | P21 - CABINET - 67x40x318cm ● Production and delivery of a cabinet made of 18mm and 25mm thick particle boards coated with white melamine foil. The sides are treated with polyurethane edging and glued with PU adhesive. All doors on the cabinet have the handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). Above the cabinet, i.e. the part for storing things, a "mask" was made with 18mm and 25mm thick particle boards to fill the space up to the ceiling, and it is also used for hanging panels, posters, etc. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 2 | 0
49. |  | P22 - PLAKAR - 91x40x318cm ● Izrada i isporuka plakara koji je izrađen od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na plakaru opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). Iznad samog plakara, odnosno dijela za skladištenje i odlaganje stvari, univerom debljine 18mm i 25mm napravljena je "maska" s ciljem popunjavanja prostora iznad plakara, do plafona, a ista služi i sa kačenje panoa, plakata i sl. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | P22 - CABINET - 91x40x318cm ● Production and delivery of a cabinet made of 18mm and 25mm thick particle boards coated with white melamine foil. The sides are treated with polyurethane edging and glued with PU adhesive. All doors on the cabinet have the handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). Above the cabinet, i.e. the part for storing things, a "mask" was made with 18mm and 25mm thick particle boards to fill the space up to the ceiling, and it is also used for hanging panels, posters, etc. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 3 | 0
50. |  | P23 - PLAKAR - 80x40x318cm ● Izrada i isporuka plakara koji je izrađen od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na plakaru opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). Iznad samog plakara, odnosno dijela za skladištenje i odlaganje stvari, univerom debljine 18mm i 25mm napravljena je "maska" s ciljem popunjavanja prostora iznad plakara, do plafona, a ista služi i za kačenje panoa, plakata i sl. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | P23 - CABINET - 80x40x318cm ● Production and delivery of a cabinet made of 18mm and 25mm thick particle boards coated with white melamine foil. The sides are treated with polyurethane edging and glued with PU adhesive. All doors on the cabinet have the handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). Above the cabinet, i.e. the part for storing things, a "mask" was made with 18mm and 25mm thick particle boards to fill the space up to the ceiling, and it is also used for hanging panels, posters, etc. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 1 | 0
51. |  | P24 - PLAKAR - 125x35x318cm ● Izrada i isporuka plakara koji je izrađen od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na plakaru opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). Iznad samog plakara, odnosno dijela za skladištenje i odlaganje stvari, univerom debljine 18mm i 25mm napravljena je "maska" s ciljem popunjavanja prostora iznad plakara, do plafona, a ista služi i za kačenje panoa, plakata i sl. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | P24 - CABINET - 125x35x318cm ● Production and delivery of a cabinet made of 18mm and 25mm thick particle boards coated with white melamine foil. The sides are treated with polyurethane edging and glued with PU adhesive. All doors on the cabinet have the handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). Above the cabinet, i.e. the part for storing things, a "mask" was made with 18mm and 25mm thick particle boards to fill the space up to the ceiling, and it is also used for hanging panels, posters, etc. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 2 | 0
52. |  | PO1 - POLICA - 546x35x200cm ● Izrada i isporuka polica koje su izrađene od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | PO1 - SHELF - 546x35x200cm ●Production and delivery of shelves made of 18mm and 25mm thick particle boards, coated with white melamine foil and the sides are treated with polyurethane edging and glued with PU glue. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 6 | 0
53. |  | PO2 - POLICA - 330x35x200cm ● Izrada i isporuka polica koje su izrađene od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | PO2 - SHELF - 330x35x200cm ●Production and delivery of shelves made of 18mm and 25mm thick particle boards, coated with white melamine foil and the sides are treated with polyurethane edging and glued with PU glue. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 4 | 0
54. |  | KO1 - KOMODA - 714x35x75cm ● Izrada i isporuka komode koja je izrađena od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na komodi opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | KO1 - COMMODE - 714x35x75cm ● Production and delivery of the commode made of 18mm and 25mm thick particle boards, coated with white melamine foil and the sides are treated with polyurethane edging and glued with PU glue. All doors on the commode are equipped with a handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). ● Check all measures on the spot. Perform according to the contractor's workshop drawings with the designer's consent. . | kom/pcs |  | 1 | 0
55. |  | KO2 - KOMODA - 500x60x90cm ● Izrada i isporuka komode koja je izrađena od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na komodi opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | KO2 - COMMODE - 500x60x90cm ● Production and delivery of the commode made of 18mm and 25mm thick particle boards, coated with white melamine foil and the sides are treated with polyurethane edging and glued with PU glue. All doors on the commode are equipped with a handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). ● Check all measures on the spot. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 1 | 0
56. |  | KO3 - KOMODA - 217x35x90cm ● Izrada i isporuka komode koja je izrađena od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na komodi opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | KO3 - COMMODE - 217x35x90cm ● Production and delivery of the commode made of 18mm and 25mm thick particle boards, coated with white melamine foil and the sides are treated with polyurethane edging and glued with PU glue. All doors on the commode are equipped with a handle (furniture knob - Ø 35mm; chrome) and lock (Z-103 - 12mm; chrome). ● Check all measures on the spot. Perform according to the contractor's workshop drawings with the designer's consent | kom/pcs |  | 1 | 0
57. |  | KU1 - KUHINJA - 222x60x200cm ● Izrada, transport i montaža kuhinje po mjeri koja je izrađena od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Otvaranje krila kao na crtežu u sklopu grafičke dokumentacije - Namještaj po mjeri, bez vidljivih ručki. Kuhinja sadrži ugradnu tehniku. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | KU1 -KITCHEN - 222x60x200cm ● Manufacture, transport and assemble the custom kitchen furniture of 18mm and 25mm thick particle boards covered with white melamine foil. The sides are treated with polyurethane edges and glued with PU glue. Opening the wings as in the graphic documentation - Furniture made to measure, without visible handles. The kitchen contains built-in the kitchen-apparatus. ● Check all measures on the spot. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 1 | 0
58. |  | Š1 - ŠANK - 182x40x90cm ● Izrada, transport i montaža šanka po mjeri koji je izrađen od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Otvaranje krila kao na crtežu u sklopu grafičke dokumentacije - Namještaj po mjeri, bez vidljivih ručki. ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | Š1 - BAR - 182x40x90cm ●Manufacture, transport, and install a custom-made bar of 18mm and 25mm thick particle boards covered with white melamine foil. The sides are treated with polyurethane edges and glued with PU glue. Opening the wings as in the graphic documentation - Furniture made to measure, without visible handles. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 1 | 0
59. |  | KL1 - KLUPA U HODNIKU - 364x94x318cm ● Izrada i isporuka plakara koji je izrađen od univera debljine 18mm i 25mm, koji je presvučen bijelom melaminskom folijom i čije se strane obrađuju poliuretanskim kantovima, a lijepe PU lijepkom. Sva vrata na plakaru opremljena su ručkom (dugme za namještaj - Ø 35mm; hrom) i bravicom (Z-103 - 12mm; hrom). Iznad samog plakara, odnosno dijela za skladištenje i odlaganje stvari, univerom debljine 18mm i 25mm napravljena je "maska" s ciljem popunjavanja prostora iznad plakara, do plafona, a ista služi i za kačenje panoa, plakata i sl. +B124 ● Sve mjere provjeriti na licu mjesta. Izvoditi prema radioničkim crtežima izvođača, uz saglasnost projektanta. | KL1 - THE BENCH IN THE CORRIDOR - 364x94x318cm ● Manufacture, transport and assembly of the custom-made bench of 2x18mm thick particle boards covered with melamine foil in the colour of light oak. The sides are treated with polyurethane edges in the same colour and glued with PU glue. Cushions are made of high-quality sponge and covered by mebl textile in grey. It is predicted to cover the walls in contact with the bench with an 18 mm thick particle board covered with melamine foil in light oak. The sides are treated with polyurethane edges of the same colour and glued with PU glue. ● Check all measures on the place. Perform according to the contractor's workshop drawings with the designer's consent. | kom/pcs |  | 4 | 0
II. |  | NAMJEŠTAJ PO MJERI | CUSTOM FURNITURE |  |  | Ukupno/Total | 0
III. |  | SPORTSKA OPREMA | SPORTS EQUIPMENT
60. |  | SO1 - GOL ZA MALI FUDBAL - 120x80cm ● Nabavka i isporuka golova za mali fudbal dimenzija 120x80cm. Konstrukcija golova je metalna, finalno obojena. Golovi se nabavljaju u kompletu sa mrežama. Uz ponudu obavezno dostaviti: - Tehnički list ponuđenog gola za mali fudbal. | SO1 - SMALL FOOTBALL GOAL - 120x80cm ● Procurement and delivery of goals for small football, size 120x80cm. The construction of the goals is metal, finished painting. The goals are purchased complete with nets. With the offer, the Contractor have to submit the following: - Technical sheet of the offered goal for indoor soccer | kom/pcs |  | 2 | 0
61. |  | SO2 - STO ZA STONI TENIS - 2740x1525x760mm ● Nabavka i isporuka stola za stoni tenis sa točkićima, dimenzija 2740x1525x760mm. Konstrukcija stola je metalna; rasklopljivi nogari (čelične cijevi zaštićene epoksidnom bojom). Ploča stola HPL minimalne debljine 19mm. U setu mrežica sa metalnim držačima, četiri reketa i deset loptica. Uz ponudu obavezno dostaviti: - Tehnički list ponuđenog stola za stoni tenis. | SO2 - TABLE TENNIS TABLE - 2740x1525x760mm ● Procurement and delivery of a table tennis table with wheels, dimensions 2740x1525x760mm. The table's structure is metal, with folding legs (steel tubes protected by epoxy paint). HPL table top with a minimum thickness of 19mm. The set contains nets with metal holders, four rackets and ten balls. With the offer, the Contractor have to submit the following: - Technical sheet of the offered table tennis table | kom/pcs |  | 1 | 0
62. |  | SO3 - PARALELNI RAZBOJ ● Nabavka i isporuka paralelnog razboja. Stabilna metalna konstrukcija osigurana ugrađenim dvostrukim osiguranjem podizne ose. Regulacija visine pritki od 120cm do 185cm; razmak između pritki od 36cm do 66cm. Uz ponudu obavezno dostaviti: - EN 12197 standard - Tehnički list ponuđenog paralelnog razboja. | SO3 - GYMNASTICS PARALLEL BARS ● Procurement and delivery of the gymnastics parallel bars. Stable metal construction secured by built-in double lifting axis insurance. Adjustment of the height of the bars from 120cm to 185cm; the distance between the bars from 36cm to 66cm. With the offer, the Contractor have to submit the following: - EN 12197 standard - Technical sheet of the offered parallel bars. | kom/pcs |  | 1 | 0
63. |  | SO4 - DVOVISINSKI RAZBOJ ● Nabavka i isporuka dvovisinskog razboja. Lagana metalna konstrukcija; jednostavna, brza i sigurna regulacija pritki napravljenih od jasenovog drveta i ojačana SVČ čelikom kvaliteta 12.21. Regulisanje visine od 110cm do 140cm, to od 190cm do 240cm; razmak između greda od 70cm do 140cm, štelujuće po osi. Uz ponudu obavezno dostaviti: - EN 915 standard; - EN 913 standard; - Tehnički list ponuđenog dvovisinskog razboja. | SO4 - GYMNASTICS DOUBLE-HEIGHT PARALLEL BARS ● Procurement and delivery of the gymnastics' double-height parallel bars. Lightweight metal construction; simple, quick and safe regulation of the abutments made of ash wood and reinforced with cold rolled steel quality 12.21. Height adjustment from 110cm to 140cm, that from 190cm to 240cm; distance between beams from 70cm to 140cm, adjustment along the axis. With the offer, the Contractor have to submit the following: - EN 915 standard; - EN 913 standard; - Technical sheet of the offered gymnastics' double-height parallel bars | kom/pcs |  | 1 | 0
64. |  | SO5 - AMERIČKI KRUGOVI ● Nabavka, isporuka i instalacija američkih krugova sa zidnom konstrukcijom napravljenom od cjevastih profila Ø60mm (montaža na visini od 5m). Konstrukcija poseduje mehanizam sa regulacijom visine karika. Uz ponudu obavezno dostaviti: - EN 913 standard; - EN 957 standard; - EN 12655 standard; - Tehnički list ponuđenih američkih krugova. | SO5 - ''AMERICAN'' GYMNASTIC CIRCUITS ● Procurement, delivery and installation of American gymnastics' circles with the wall structure of tube profiles Ø60mm (assembly at 5m). The system has a mechanism with link height regulation. With the offer, the Contractor have to submit the following: - EN 913 standard; - EN 957 standard; - EN 12655 standard; - Technical sheet of offered American circuits | kom/pcs |  | 1 | 0
65. |  | SO6 - PENJALICE ● Nabavka, isporuka i instalacija konstrukcije za penjalice sa 3 mjesta kačenja. U setu jedan kanap dužine 5m, jedna motka (metalna) dužine 5m i jedne mornarske merdevine dužine 4m. Uz ponudu obavezno dostaviti: - EN 913 standard; - EN 12346 standard; - Tehnički list ponuđene penjalice. | SO6 - CLIMBING FRAMES ● Procurement, delivery and installation of the structure for climbing frames with three hanging points. The set includes one rope 5m long, one pole (metal) 5m long and one sailor's ladder 4m long. With the offer, the Contractor have to submit the following: - EN 913 standard; - EN 12346 standard; - Technical sheet of the climbing equipment offered. | kom/pcs |  | 1 | 0
66. |  | SO7 - ODSKOČNA DASKA ● Nabavka, isporuka i instalacija odskočne rojter daske izrađene od posebno vezane ploče sa odskočnom površinom prekrivenom kvalitetnom tapaciranom oblogom. Visina prednjeg dijela odskočne daske 15cm. Uz ponudu obavezno dostaviti: - EN 913 standard; - Tehničli list ponuđene odskočne daske. | SO7 - SPRINGBOARD ● Procurement, delivery and installation of the Reuter springboard made of specially bonded boards with a springboard surface covered with high-quality upholstery. The height of the front part of the springboard is 15cm. With the offer, the Contractor have to submit the following: - EN 913 standard; - Technical sheet of the offered springboard | kom/pcs |  | 1 | 0
67. |  | SO8 - JUNIOR KOZLIĆ ● Nabavka i isporuka junior kozlića od kože. Metalne noge sa teleskopskom regulacijom visine od 90cm do 110cm. Na metalnim nogama se nalaze gumene navlake koje sprečavaju klizanje sprave. Korpus kozlića presvučen kožom. Uz ponudu obavezno dostaviti: - EN 913 standard - EN 12196 standard - Tehnički list ponuđenog junior kozlića. | SO8 - JUNIOR VAULTING HORSE ● Procurement and delivery of the Junior vaulting horse. Metal legs with telescopic height regulation from 90cm to 110cm. The metal legs have rubber covers that prevent the device from slipping. The body of the vaulting horse is covered with leather. With the offer, the Contractor have to submit the following: - EN 913 standard - EN 12196 standard - Technical sheet of offered junior vaulting horse | kom/pcs |  | 1 | 0
68. |  | SO9 - SENIOR KOZLIĆ ● Nabavka i isporuka senior kozlića od kože. Metalne noge sa teleskopskom regulacijom visine od 90cm do 130cm. Na metalnim nogama se nalaze gumene navlake koje sprečavaju klizanje sprave. Korpus kozlića presvučen kožom. Uz ponudu obavezno dostaviti: - EN 913 standard; - EN 12196 standard; - Tehnički list ponuđenog senior kozlića. | SO9 - SENIOR VAULTING HORSE ● Procurement and delivery of the senior vaulting horse. Metal legs with telescopic height regulation from 90cm to 130cm. The metal legs have rubber covers that prevent the device from slipping. The body of the vault is covered with leather. With the offer, the Contractor have to submit the following: - EN 913 standard; - EN 12196 standard; - Technical sheet of the offered senior vaulting horse | kom/pcs |  | 1 | 0
69. |  | SO10 - ŠVEDSKA KLUPA ● Nabavka i isporuka drvene švedske klupe dimenzija 4000x250x350mm. Materijal jela/smrča. Površinska obrada: lakirano poliuretanskim lakom. Uz ponudu obavezno dostaviti: - EN 913 standard - EN 916 standard - Tehnički list ponuđene švedske klupe. | SO10 - THE SWEDISH GYM BENCH ● Procurement and delivery of the wooden Swedish bench with dimensions 4000x250x350mm. Material fir/spruce. Surface treatment: varnished with polyurethane varnish. With the offer, the Contractor have to submit the following: - EN 913 standard - EN 916 standard - Technical sheet of the offered Swedish bench. | kom/pcs |  | 4 | 0
70. |  | SO11 - ŠVEDSKI 5-DJELNI SANDUK ● Nabavka i isporuka drvenog švedskog 5-djelnog sanduka dimenzija 1500x1100x500mm. Ugaonici i stopa od parene bukve, stranice od jele/smrče. Lakiran poliuretanskim lakom. Mogućnost prilagođavanja visine dodavanjem ili vađenjem djelova. Gornji dio tapaciran zimom i presvučen kvalitetnim skajem. Uz ponudu obavezno dostaviti: - EN 913 standard; - EN 916 standard; - Tehnički list ponuđenog švedskog sanduka. | SO11 - SWEDISH 5-PART GYM VAULTING BOX ● Procurement and delivery of the wooden Swedish 5-part vaulting box measuring 1500x1100x500mm. Corners and feet made of steamed beech, sides made of fir/spruce. Finally treated with polyurethane varnish. Possibility to adjust the height by adding or removing parts. The upper part is upholstered and covered with quality artificial leather With the offer, the Contractor have to submit the following: - EN 913 standard; - EN 916 standard; - Technical sheet of the offered Swedish box | kom/pcs |  | 1 | 0
71. |  | SO12 - ZIDNO VRATILO ● Nabavka, isporuka i instalacija zidnog vratila. Konstrukcija od valjanog čelika, drvena pritka i lanac. Uz ponudu obavezno dostaviti: - EN 913 standard; - EN 916 standard; - Tehnički list ponuđenog zidnog vratila. | SO12 - GYM WALL SHAFT FOR PULL-UP ● Procurement, delivery and installation of the wall shaft. Rolled steel construction, wooden attachment and chain. With the offer, the Contractor have to submit the following: - EN 913 standard; - EN 916 standard; - Technical sheet of the offered wall shaft | kom/pcs |  | 1 | 0
72. |  | SO13 - VISOKA GREDA ● Nabavka i isporuka visoke grede dimenzija 5000x1200x130mm. Materijal: jela/smrča, čelična cijev Ø42mm. Površinska obrada: drvo brušeno, finalno zaštićeno, metal plastificiran, gumene navlak za stope. Uz ponudu obavezno dostaviti: - EN 913 standard; - EN 915 standard; - EN 12432 standard; - Tehnički list ponuđene visoke grede. | SO13 - HIGH BEAM ● Procurement and delivery of the high beam measuring 5000x1200x130mm. Material: fir/spruce, steel tube Ø42mm. Surface treatment: sanded wood, finally protected, plasticized metal, rubber cover for the feet. With the offer, the Contractor have to submit the following: - EN 913 standard; - EN 915 standard; - EN 12432 standard; - Technical sheet of the offered high beam. | kom/pcs |  | 1 | 0
73. |  | SO14 - GIMNASTIČKA STRUNJAČA ● Nabavka i isporuka gimnastičkih strunjača za ripstole dimenzija 164x82x6cm sa čičkom za kačenje. Navlaka izrađena od PVC tkanine sa donjom protivkliznom stranom. Punjenje: žima ili regenerat sunđera i žima. Uz ponudu obavezno dostaviti: - EN 913 standard; - EN 12503 standard; - Tehnički list ponuđene strunjače za ripstol. | SO14 - GYMNASTIC MAT ● Procurement and delivery of gymnastic mats for ripstol (Swedish ladder) measuring 164x82x6cm with velcro for hanging. Cover made of PVC textile with the non-slip bottom side. Filling: cotton or regenerated sponge and cotton. With the offer, the Contractor have to submit the following: - EN 913 standard; - EN 12503 standard; - Technical sheet of the offered gymnastic mat for ripstol. | kom/pcs |  | 20 | 0
74. |  | SO15 - ORMAR ZA REKVIZITE ● Nabavka i isporuka metalnog ormara za sportske rekvizite dimenzija 80x50x200cm. Izrađen od grifovanog pletiva 50x50mm, L profila 25x25mm i 20x20mm. Drvene police od vodootpornog špera debljine 20mm. Završno plastificirano. Uz ponudu obavezno dostaviti: - Tehnički list ponuđenog metalnog ormara za rekvizite. | SO15 - CABINET FOR SPORTS PROPS ● Procurement and delivery of a metal cabinet for sports props, dimensions 80x50x200cm. Made of knitted mesh 50x50mm, L profile 25x25mm and 20x20mm. Wooden shelves made of waterproof plywood 20mm thick. Finally, treatment is plasticized. With the offer, the Contractor have to submit the following: - Technical sheet of the offered metal cabinet for props. | kom/pcs |  | 2 | 0
75. |  | SO16 - SET ZA ODBOJKU ● Nabavka, isporuka i ugradnja seta za odbojku. Stubovi konstrukcije (usadni) su aluminijumski min. Ø100mm i potrebno je da imaju mekanu demontažnu zaštitu. Mreža je pletena 4mm, sa oknima 100mm, oivičena platnom širine 50mm, sa mehanizmom za napinjanje i podešavanja mreže po visini za različite uzraste. U kompletu 2 antene. Boja meke zaštite stubova po izboru investitora. Uz ponudu obavezno dostaviti: - EN 1271 standard - Tehnički list ponuđenog seta za odbojku. | SO16 - VOLLEYBALL SET ● Procurement, delivery and installation of volleyball sets. The pillars of the structure (inserts) are aluminium min. Ø100mm, and they need to have soft removable protection. The net is knitted 4mm, with 100mm holes, edged with a 50mm wide canvas, with the mechanism for tensioning and adjusting the net height for different ages. 2 antennas are included. The investor chooses the colour of the soft protection of the pillars. With the offer, the Contractor have to submit the following: - EN 1271 standard - Technical sheet of the offered volleyball set. | kom/pcs |  | 1 | 0
76. |  | SO17 - ALUMINIJSKI RUKOMETNI GOL ● Nabavka, isporuka i ugradnja aluminijumskog rukometnog gola sa sklopivom toplo cinkovanom konstrukcijom dubine 100-120cm sa glavnom i pomoćnom mrežom i podnim pričvršćivanjem. Pričvršćivanje rukometnog gola na sportski pod. Uz ponudu obavezno dostaviti: - EN 749 standard - IHF sertifikat - Tehnički list ponuđenog rukometnog gola. | SO17 - ALUMINUM HANDBALL GOAL ● Procurement, delivery and installation of the aluminium handball goal with a collapsible hot-dip galvanized structure 100-120cm deep, with the main and auxiliary net and floor fixing. Fixing the handball goal to the sports floor. With the offer, the Contractor have to submit the following: - EN 749 standard - IHF certificate - Technical sheet of the offered handball goal.. | kom/pcs |  | 2 | 0
77. |  | SO18 - ZIDNI SKLOPIVI KOŠ ● Nabavka, isporuka i montaža zidnog, bočno pomičnog (sklopivog) koša. Konstrukcija metalna. Ploča udaljena max 3,25m od zida. Koš bočno sklopiv, ručno sklapanje, mehanička kočnica u otklopljenom i sklopljenom stanju. Tabla staklena sekurit dimenzija 180cm x 105cm sa izrezom, mekana zaštita donjeg ruba i dijela bočnog, obruč sa oprugom (pregibni), mrežica takmičarska. Posjeduje i mehaničku zaštitu od pada kao i regulaciju visine obruča od 260cm do 305cm. Boja konstrukcije i meke zaštite staklene table po izboru investitora. Uz ponudu obavezno dostaviti: - EN 1270 standard - Tehnički list ponuđenog zidnog sklopivog koša. | SO18 - WALL-FOLDING BASKETBALL BASKET ● Procurement, delivery and installation of a wall-mounted, sideways movable (collapsible) basket. Metal construction. The plate is at the maximum distance of 3.25 m from the wall. Side folding basket, manual-folding, mechanical brake in unfolded and folded state. Security glass board, dimensions 180cm x 105cm with cut-out, soft protection of the lower edge and part of the side, the ring with spring (folding), and the competitive mesh. It has mechanical fall protection and hoop height regulation from 260cm to 305cm. The investor's choice is the colour of the construction and the soft protection of the glass panel. The following have to be submitted with the offer: - EN 1270 standard - Technical sheet of the offered wall folding basket. | kom/pcs |  | 2 | 0
78. |  | SO19 -FIKSNI ZIDNI KOŠ ● Nabavka, isporuka i montaža zidnog, fiksnog koša u fiskulturnoj sali. Konstrukcija metalna. Ploča udaljena max 0,50m od zida. Tabla drvena dimenzija 120cm x 60cm, obruč fiksni, mrežica takmičarska. Boja konstrukcije po izboru investitora. Uz ponudu obavezno dostaviti: - Tehnički list ponuđenog zidnog fiksnog koša. | SO19 -FIXED WALL BASKETBALL BASKET ● Procurement, delivery and installation of a wall-mounted, fixed basket in the sports hall. Metal construction. The board is at the maximum distance of 0.50m from the wall. Wooden board dimensions 120cm x 60cm, fixed hoop, competitive mesh. The investor chooses the colour of the construction. Have to be submitted with the offer : - Technical sheet of the offered fixed wall basket. | kom/pcs |  | 2 | 0
III. |  | SPORTSKA OPREMA | SPORTS EQUIPMENT |  |  | Ukupno/Total | 0
11 . |  | REKAPITULACIJA - PROJEKAT OPREMANJA ŠKOLE I SALE | SUMMARY - DESIGN OF FURNITURE AND EQUIPMENT FOR SCHOOL AND HALL
I. |  | SERIJSKA OPREMA | SERIAL EQUIPMENT |  |  |  | 0
II. |  | NAMJEŠTAJ PO MJERI | CUSTOM FURNITURE |  |  |  | 0
III. |  | SPORTSKA OPREMA | SPORTS EQUIPMENT |  |  |  | 0
11. |  | UKUPNO - PROJEKAT OPREMANJA ŠKOLE I SALE | TOTAL - DESIGN OF FURNITURE AND EQUIPMENT FOR SCHOOL AND HALL |  |  |  | 0